Product Name: Altivar 212

Adjustable Frequency AC Drive for Variable Torque HVAC and Pumping Applications, Open or Type 1

Ready to mount in an enclosure or requiring Type 1 wall mounting enclosure rating detailed below:

1-40 hp @ 200/240 V, 1-100 hp @ 380/480 V:

IP 41 on top IP21 on all other surfaces, Type 1 with optional conduit kit.

Copies of this specification are available from the Product Specification section of the Technical Library at the  Schneider Electric website:

http://products.schneider-electric.us/support/technical-library/?event=type.list&docType=sqd_csi_spec

### SECTION 26 29 23.13 {Electrical} OR 23 09 33 {Mechanical}

### Adjustable Frequency Drives for HVAC and Pumping Applications

PART 1: GENERAL

1.01 SUMMARY

A.	This section provides specification requirements for solid-state, pulse-width modulated (PWM) Adjustable Frequency Drives, herein referred to as AC Drives, for use with NEMA® design  [NEMA A] [NEMA B] [NEMA D] [NEMA E] AC motors, or standard IEC motors.

B.	The AC Drive supplier shall furnish, field test, adjust and certify all installed AC Drives for satisfactory operation.

C.	Any exceptions/deviations to this specification shall be indicated in writing and submitted no less than one week prior to bid date.

1.02 REFERENCES

- ANSI®/NFPA® 70 - National Electrical Code® (NEC®).

- UL 508 - UL Standard for Safety Industrial Control Equipment.

- UL 508C - UL Standard for Safety Power Conversion Equipment.

- UL1995 - Plenum rating

- NEMA ICS 7: Adjustable Speed Drives Safety Standards

- CSA C22.2 No. 14-M91 : Industrial Control Equipment

- IEC 60068-2: Environment compliance for humidity, vibration, and shock

- IEC 61800 : Adjustable speed Electrical power drive systems

- IEC 61000-3-12:  Limits for Harmonic Current

1.03 SUBMITTALS

A.	A submittal package shall be furnished for the Engineers’ approval.  This package shall consist of elementary power and control wiring diagrams and outline drawings. The outline drawings shall include front and side views of with overall dimensions and weights shown. . Standard catalog specification sheets showing voltage, horsepower and maximum current ratings shall be furnished as part of the submittal package.

1.04 WARRANTY

A.	An 18-month warranty shall be provided on materials and workmanship from the date of shipment.

1.05 QUALITY ASSURANCE

A.	The manufacturer of the AC Drive shall be a certified ISO 9001/14001 facility.

B.	The AC Drive and all associated optional equipment shall be UL Listed according to UL 508 C - Power Conversion Equipment. As verification, a UL label shall be attached on the nameplate.

C.	The AC Drive shall be designed, constructed and tested in accordance with applicable UL, CSA, IEC, NEMA, and NEC standards.

D.	Every power converter shall have serial number with traceability records maintained by the manufacture.

## PART 2: PRODUCT

2.01 MANUFACTURERS

A.	The AC Drive shall be manufactured by Schneider Electric or prior approved equal. Substitutions must be submitted in writing three weeks prior to original bid date with supporting documentation demonstrating that the alternative manufacturer meets all aspects of the specifications herein.   Supporting documentation should include a line by line review of this specification indicating if the substitution meets or does not meet each item in this specification.

2.02 GENERAL DESCRIPTION

A. The AC Drive shall convert the input AC mains power to an adjustable frequency and voltage.

B. The input power section shall utilize a full wave bridge design incorporating diode rectifiers. The diode rectifiers shall convert fixed voltage and frequency, AC line power to fixed DC voltage.

C. The output power section shall change fixed DC voltage to adjustable frequency AC voltage.

D. The AC drive shall include terminals strip for hardwire connection of analog or voltage speed

reference signal, start stop control and fault reset.

E.  The AC drive shall include terminal strip connection to [BACnet] [Johnson Controls Metasys N2] [Siemens Apogee P1] [Modbus] [Lonworks by internal option card].

F. The AC drive shall have an integrated user interface (keypad) to display information, provide status, and allow configuration and local operation of the drive.  The user interface shall include a Local / Remote button to switch between control at the terminal strip and the user interface (keypad).   This button shall also switch between network control and the user interface (keypad).  The keypad shall have Run and Stop keys and a manual speed potentiometer function. [A remote LCD 8 line, 24 character per line, English text keypad display shall be included and be mounted near the drive].

2.03 CONSTRUCTION

A.	The AC Drive shall comply with NEMA ICS 7 and IEC 61800 -2 Adjustable Speed Drives Safety Standards for ratings, construction, testing, performance and manufacturing.

B.	The AC Drive power converter shall be constructed of materials to comply with RoHS (Restriction of Hazardous Substances) directive for electrical equipment.

C.	The AC Drive power converter shall be UL Plenum rated.

- All heat sink fans shall be accessible and shall not require the removal of the AC drive power converter for fan replacement.

- The AC Drive shall have galvanic isolation between power and control inputs, outputs and power supplies.

- The AC Drive shall be constructed without DC chokes, swinging chokes, and be designed to operate without the need for external AC line reactors, to improve the AC Drive – motor operating efficiency.  Harmonic current distortion of the AC Drive shall be equal to harmonic abatement obtained by using DC chokes, swinging chokes, or 3% AC line reactors.

- The AC Drive motor control firmware shall have an energy economizer function that will reduce the voltage to the motor after set speed is obtained and optimize motor power usage and efficiency.. A constant volts/Hz ratio will be maintained during acceleration. When set speed is obtained the output voltage will then automatically adjust to meet the torque requirement of the load.

- The AC Drive shall have the an enclosure protection rating of IP 41 on top IP21 on all other surfaces, [ the AC Drive shall include an optional conduit kit to provide a Type 1 rated enclosure. ]

- When a Type 1 conduit entrance kit is required.  The kit shall attach and be ground to the bottom of the AC drive and provide conduit landing for incoming line power cables, motor lead cable, control wiring, and network cabling.

2.04 APPLICATION DATA

A.	The AC Drive shall be sized to operate a variable torque load and be rated to provide 110% overload for 60 seconds.

B.	The speed range shall be from a minimum speed of 1.0 Hz to a maximum speed of 72 Hz.

2.05 ENVIRONMENTAL RATINGS

- The AC Drive shall comply with IEC 60068-2 environmental standard.

- The AC Drive shall be designed to operate in an ambient temperature from -10 to 40 ˚C (14 to 104 ˚F).  Rating for operation up to 60 ˚C (140 ˚F) shall be published by the manufacture.

- AC Drives in Type 1 enclosures shall be designed to operate in an ambient temperature from -10 to 40 ˚C (14 to 104 ˚F).

D.	The storage temperature range shall be -25 to 65 ˚C (-13 to 149 ˚F).

E.	The AC Drive shall comply with IEC 60068-2-3 for operation in humid environments up to 95%, non-condensing.

F.	The AC Drive shall be rated to operate at altitudes less than or equal to 3300 ft (1000 m). For altitudes above 3300 ft (1000 m), the AC Drive should be de-rated by 1% for each 330 ft (100 m) up to 10,000 ft (3000 m).

G.	The AC Drive shall meet the IEC 60068-2-6 and 60068-2-8 vibration specification and conform to IEC 60068-2-27 shock specification.

2.06 RATINGS

A.	The AC Drive shall be designed to operate at the input line voltage of:

200V -15% to 240 V + 10% or 380V-15% to 480V+10%.

B.	The AC Drive shall operate from an input frequency range of 50 or 60 Hz (±) 5%.

C.	The displacement power factor shall not be less than .98 lagging under any speed or load condition.

D.	The AC Drive input current ratings shall not exceed the AC Drive output current ratings.

E.	The efficiency of the AC Drive at 100% speed and load shall not be less than 98%.

F.	The variable torque rated AC Drive over current capacity shall be not less than 110% for 1 minute.

G.	The output carrier frequency of the AC Drive shall be selectable from 6 to 16 kHz. 
12kHz nominal rating for 1-20 hp @ 200/240 V, 1-20 hp @ 380/480 V.

8kHz nominal rating for >20-40 hp @ 200/240 V, >20-100 hp @ 380/480 V.

2.07 PROTECTION

A.	Upon power-up, the AC Drive shall automatically test for valid operation of memory, loss of analog reference input, loss of communication, DC-to-DC power supply, control power and pre-charge circuit.

B.	The AC drive shall be rated for UL minimum short circuit currents per given horsepower rating.

C.    The AC Drive manufacture shall supply branch circuit protection recommendations, tested per UL 508C,  to achieve up to 100k short circuit current rated installation.

D.	The AC Drive shall provide protection on the output against short circuits between output phases and output phase to ground.

E.	The AC drive shall have a programmable power loss functionality to ride through momentary line power dips or loss.  The function shall allow the drive to capture regenerative energy from the motor and connected load, monitor motor speed, and smoothly ramp the motor back to specified speed upon restoration of line power.

F.	The AC drive shall have an auto restart function with a selectable number, (up to 10) of  restart attempts. The restart shall be attempted after the fault has disappeared and other operating conditions permit the restart.  The restart shall be performed by a series of automatic attempts, adding a 1 sec delay to each restart attempt, until the programmed number of restart attempts has been reached. The AC drive fault relay response shall be configurable to signal a detected fault or not indicate a detected fault.

G.	The AC Drive shall have loss of the analog process follower reference signal detection with configurable response. The AC Drive shall be configured to [freewheel stop] [go to a configured preset speed of xx] [maintain speed at the time of signal loss] [ramp to stop].

H.    The AC Drive shall have under load detection functionality with configurable alarming features to respond to loss of flow condition.

H.	The AC Drive shall have a solid-state UL 508C listed overload protective device.

I.	The output frequency shall be software enabled to fold back when the motor is overloaded.

J.	The AC Drive shall have three skip frequency ranges that can be programmed to a bandwidth of 30 Hz.

2.08 ADJUSTMENTS & CONFIGURATIONS

A.	The AC drive shall have an integrated user interface to allow configuration and adjustment of parameters.

B.	The AC Drive shall allow configurations to be stored in an optional, portable hand-held device to allow easy up loading, down loading and storage of the AC drive  configuration.

B.	The AC Drive shall manufacture shall provide PC software that provides configuration, up-load, down-load and AC drive monitoring capabilities.  The PC software shall have the capability to save and store individual configuration files.

C.	The memory shall retain and record run status and fault type of the past four faults.

D.	The AC Drive shall have internal configurable PID control functionality.

E.	The AC Drive shall have internal configurable damper control functionality

E.	The AC Drive shall have macro configurations for typical HVAC and pump control wiring configurations.

2.09 KEYPAD DISPLAY INTERFACE

A.	The AC Drive shall include LED status indicators for:  power on, run, programming and monitoring mode.

B.	A keypad display interface shall offer the modification of AC Drive adjustments through a touch keypad. Electrical values, configuration parameters, I/O assignments, application and activity function access, faults, local control, and adjustment storage, and diagnostics shall be accessible via the keypad. [A remote LCD 8 line, 24 character per line, English text keypad display shall be included and be mounted near the drive]

- The keypad display shall have parameter lock capability that allows the keypad to be locked out from unauthorized personnel.

- The keypad shall be capable of displaying I/O assignment and status.

2.10 CONTROL CONNECTIONS

A.	The control power for the digital inputs and outputs shall be 24Vdc.

B.	The internal power supply shall incorporate automatic current fold-back that protects the internal power supply if incorrectly connected or shorted. The transistor logic outputs will be current limited and will not be damaged if shorted.

C.	Two voltage-free relay output contacts (1 NO/NC, 1 NO)  will be provided. One of the contacts will indicate AC Drive fault status. The other contact shall indicate a drive run status. These relays shall be configurable for other status indicators.

- The AC drive shall have three logic inputs, two analog inputs, one analog output.

- The control section of AC drive shall be supplied separately if necessary with 24Vdc.

.

2.11 SERIAL COMMUNICATION

- The AC Drive shall have an integrated RJ45 port, for connection to a remote keypad, Bluetooth receiver, or PC Soft pc software.

- The AC drive shall have the capability for internal connection to communication networks. The following protocols shall be available :

| Industrial Installations | HVAC building Installations |
| --- | --- |
| - Modbus | -Lonworks (via internal option card) -BACnet -METASYS N2 -APOGEE FLN |

2.12 HARMONIC MITIGATION

A.	The AC Drive shall comply with IEC 61000-3-12:  Limits for Harmonic Current.

B.    Harmonic current distortion of the AC Drive shall be equal to harmonic abatement obtained by using DC chokes, swinging chokes, or 3 % AC line reactor without requiring additional panel space.

# PART 3: INSTALLATION

3.01	INSPECTION

A.	Verify that the location is ready to receive work and the dimensions are as indicated.

3.02	PROTECTION

A.	Before and during the installation, the AC Drive equipment shall be protected from water and site contaminants.

3.03	INSTALLATION

A.	Installation shall be in compliance with manufacturer's instructions, drawings and recommendations.

B.	The AC Drive supplier shall provide a representative to inspect the contractor's installation, test and start-up the AC Drive(s) furnished under this specification.

3.04	TRAINING

A.	On-site training shall be provided as part of the start-up service.

3.05	DOCUMENTATION

A.	The AC Drive supplier shall supply a comprehensive bound instruction and installation manual that includes wiring diagrams, layout diagrams, and outline dimensions. This manual must be insertion in a shop manual supplied by the installing contractor.