## Instructions
NNZ85544 | V1.1 | ATS480 - Communication Parameters
/!\ WARNING
UNEXPECTED MOVEMENT Device systems may perform unexpected movements because of incorrect wiring, incorrect settings, incorrect data or other errors. • Only appropriately trained persons who are familiar with and understand the contents of all pertinent product documentation and who have received safety training to recognize and avoid hazards involved are authorized to work on and with this device system. Installation, adjustment, repair and maintenance must be performed by qualified personnel. • Carefully install the wiring in accordance with the EMC requirements. • Do not operate the product with unknown or unsuitable settings or data. • Perform a comprehensive commissioning test. Failure to follow these instructions can result in death, serious injury, or equipment damage.
/!\ WARNING
LOSS OF CONTROL • The designer of any control scheme must consider the potential failure modes of control paths and, for critical control functions, provide a means to achieve a safe state during and after a path failure. Examples of critical control functions are emergency stop, overtravel stop, power outage and restart. • Separate or redundant control paths must be provided for critical control functions. • System control paths may include communication links. Consideration must be given to the implications of unanticipated transmission delays or failures of the link. • Observe all accident prevention regulations and local safety guidelines (1). • Each implementation of the product must be individually and thoroughly tested for proper operation before being placed into service. Failure to follow these instructions can result in death, serious injury, or equipment damage.
Note a.: For additional information, refer to NEMA ICS 1.1 (latest edition), “Safety Guidelines for the Application, Installation, and Maintenance of Solid State Control” and to NEMA ICS 7.1 (latest edition), “Safety Standards for Construction and Guide for Selection, Installation and Operation of Adjustable-Speed Device Systems.”
Electrical equipment should be installed, operated, serviced, and maintained only by qualified personnel. No responsibility is assumed by Schneider Electric for any consequences arising out of the use of this material.
EXPLANATORY NOTE
This Excel file is for reference only. Refer to programming manual and communication protocols manuals for full information.
This Excel file can be used to carry out searches (example: parameter address and format) and sort operations.
The columns include the following criteria:
Code: Language-independent, this allows a rapid search in the programming manual, which includes an index of parameter codes.
Additional information can be found in the Communication Manuals (Modbus, CANopen....etc.....)
Name: Parameter designation
Logic address: Address for the Modbus messaging are in decimal and hexadecimal (preceded by 16#) format.
To optimize Modbus messaging performance, two addresses are given for the control word (CMD) and the status word (ETA).
The addresses annotated "speed" are for use in rpm; the addresses annotated "frequency" are for use in Hz.
CANopen index: CANopen index/subindex in hexadecimal format, to be used for variable assignment of PDOs and SDO messaging.
PROFIBUS index: Address for PROFIBUS
CIP : Address for DeviceNet
Class/instance/attribute in decimal and hexadecimal (preceded by 16#) format.
When two paths are given, for example:
- 16#29/01/0D = 41/1/13 (messaging): ODVA standard path. It can be used for explicit messaging. Do not use it for configuring an assembly.
- 16#8C/01/07 = 140/1/7 (assembly): Altivar-specific path. This is the path that must be used for configuring an assembly. Avoid using it for explicit messaging, to ensure better interchangeability.
Link: For WORD type parameters, a dynamic link opens the description of a bit register or a listing. Listings are common to several parameters; only one part is valid for a given parameter. Refer to programming manual to determine the valid values. If an invalid value is written to a configuration parameter, the device will indicate a fault [Invalid config.] (CFI).
Category: Defines the role of the parameter, for example: Command parameter, Status parameter, etc.
Access: Read and write options:
R: Read only
R/W: Read and write
R/WS: Read and write (write only possible when the device is not in RUN mode).
It is not possible to write these parameters in "5-Operation enabled" or "6-Quick stop active" states.
If the parameter is written in the "4-Switched on" state, transition 10 to "2-Switch on disabled" is activated.
Type:
WORD (bit register): Word where each bit represents a command or a state
WORD (listing): Word where each value represents a possible choice for a configuration or state
INT: Signed integer
UINT: Unsigned integer
DINT: Signed double integer
UDINT: Unsigned double integer
Units: Physical unit and multiplier
Factory setting: Value of the parameter set at the factory.
Menu: Indicates the menus or menus where the parameter is located. Menu name displayed on the graphic display terminal, in square brackets [---], and menu code displayed by the 7-segment digits on the integrated display terminal, in round brackets (---).
Range: Possible values
Display: Parameter name displayed on the graphic display terminal, in square brackets [---], and parameter code displayed by the 7-segment digits on the integrated display terminal, in round brackets (---).
Menu: Indicates the menus or menus where the parameter is located. Menu name displayed on the graphic display terminal, in square brackets [---], and menu code displayed by the 7-segment digits on the integrated display terminal, in round brackets (---).
Order: Gives the initial storage order of the parameter in the file, from 1 to n. This makes it possible, after sorting operations, to put this file back in its initial order by sorting the column in ascending order.

## Parameters
Code | Name | Logic address | CANopen index | CIP path | Link | Category | Access | Type | Units | Factory setting | Range | Display | Menu
CMI | Extended control word | 16#2138 = 8504 | 16#2037/5 | 16#8B/01/69 = 139/01/105 |  | Control parameters | R/W | WORD (BitString16) | -
CMD | Command register | 16#2135 = 8501 | 16#2037/2 | 16#8B/01/66 = 139/01/102 |  | Control parameters | R/W | WORD (BitString16) | - |  |  | [Cmd Register] (CMD) | [Communication map] (CMM)
RPR | Counter reset | 16#0C30 = 3120 | 16#2001/15 | 16#70/01/79 = 112/01/121 | RPR | Control parameters | R/W | WORD (Enumeration) | - | [No] NO |  | [Counter Reset] (RPR) | [Counter Management] (ELT) [Energy parameters] (ENP)
ETA | Status Register | 16#0C81 = 3201 | 16#2002/2 | 16#71/01/02 = 113/01/02 |  | Status parameters | R | WORD (BitString16) | - |  |  | [Status Register] (ETA) | [Communication map] (CMM)
HMIS | Device state | 16#0CA8 = 3240 | 16#2002/29 | 16#71/01/29 = 113/01/41 | HMIS | Status parameters | R | WORD (Enumeration) | -
ETI | Internal State register | 16#0C86 = 3206 | 16#2002/7 | 16#71/01/07 = 113/01/07 |  | Status parameters | R | WORD (BitString16) | -
CCC | Active command channel | 16#20FA = 8442 | 16#2036/2B | 16#8B/01/2B = 139/01/43 |  | Status parameters | R | WORD (BitString16) | -
CNFS | Active configuration | 16#1F54 = 8020 | 16#2032/15 | 16#89/01/15 = 137/01/21 | CNFS | Status parameters | R | WORD (Enumeration) | -
LCR | Motor current | 16#0C84 = 3204 | 16#2002/5 | 16#71/01/05 = 113/01/05 |  | Actual values parameters | R | UINT (Unsigned16) | 0.1 A |  | 0.0 A ... 6553.5 A | [Motor Current] (LCR) | [Motor parameters] (MMO)
THR | Motor thermal state | 16#259E = 9630 | 16#2042/1F | 16#91/01/1F = 145/01/31 |  | Measurement parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 300 % | [Motor Therm State] (THR) | [Thermal Monitoring] (TPM)
RTH | Motor run time | 16#0CAC = 3244 | 16#2002/2D | 16#71/01/2D = 113/01/45 |  | Measurement parameters | R | UINT (Unsigned32) | 1 s |  | 0 s ... 4294967295 s
PTH | Power-on time | 16#0CAE = 3246 | 16#2002/2F | 16#71/01/2F = 113/01/47 |  | Measurement parameters | R | UINT (Unsigned32) | 1 s |  | 0 s ... 4294967295 s
IL1R | Logic inputs states | 16#1452 = 5202 | 16#2016/3 | 16#7B/01/03 = 123/01/03 |  | I/O parameters | R | WORD (BitString16) | -
OL1R | Logic outputs states | 16#145C = 5212 | 16#2016/D | 16#7B/01/0D = 123/01/13 |  | I/O parameters | R/W | WORD (BitString16) | -
AI1C | Physical value AI1 | 16#147A = 5242 | 16#2016/2B | 16#7B/01/2B = 123/01/43 |  | I/O parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
AI1R | Analog input 1 standardized value | 16#1470 = 5232 | 16#2016/21 | 16#7B/01/21 = 123/01/33 |  | I/O parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
AO1C | AQ1 physical value | 16#1497 = 5271 | 16#2016/48 | 16#7B/01/48 = 123/01/72 |  | I/O parameters | R/W | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
AO1R | Analog output 1 standardized value | 16#148D = 5261 | 16#2016/3E | 16#7B/01/3E = 123/01/62 |  | I/O parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
ERRD | CiA402 fault code | 16#219E = 8606 | 16#2038/7 | 16#8C/01/07 = 140/01/07 | ERRD | Fault parameters | R | WORD (BitString16) | -
LFT | Last error occurred | 16#1BD1 = 7121 | 16#2029/16 | 16#84/01/7A = 132/01/122 | LFT | Fault parameters | R | WORD (Enumeration) | - |  |  | [Last Error] (LFT) | [Diag. data] (DDT)
CIC | Incorrect configuration | 16#1BDA = 7130 | 16#2029/1F | 16#84/01/83 = 132/01/131 |  | Fault parameters | R | WORD (BitString16) | -
CNF | Fieldbus module Communication interruption | 16#1BDC = 7132 | 16#2029/21 | 16#84/01/85 = 132/01/133 |  | Fault parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Fieldbus Com Interrupt] (CNF) | [Ethernet Module Diag] (MTE) [PROFIBUS DIAG] (PRB)
ILF1 | Internal communication interruption 1 | 16#1BDE = 7134 | 16#2029/23 | 16#84/01/87 = 132/01/135 |  | Fault parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [InternCom Error1] (ILF1) | [Ethernet Module Diag] (MTE) [PROFIBUS DIAG] (PRB)
FNB | Fault counter | 16#1CE1 = 7393 | 16#202B/5E | 16#85/01/C2 = 133/01/194 |  | Fault parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DP0 | Fault code on last fault | 16#1C20 = 7200 | 16#202A/1 | 16#85/01/01 = 133/01/01 | LFT | History parameters | R | WORD (Enumeration) | -
LCP0 | Motor current | 16#1C48 = 7240 | 16#202A/29 | 16#85/01/29 = 133/01/41 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
THP0 | Motor thermal state | 16#1C70 = 7280 | 16#202A/51 | 16#85/01/51 = 133/01/81 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 %
EP0 | State word | 16#1C2A = 7210 | 16#202A/B | 16#85/01/0B = 133/01/11 |  | History parameters | R | WORD (BitString16) | -
IP0 | ETI state word | 16#1C34 = 7220 | 16#202A/15 | 16#85/01/15 = 133/01/21 |  | History parameters | R | WORD (BitString16) | -
CMP0 | Cmd word | 16#1C3E = 7230 | 16#202A/1F | 16#85/01/1F = 133/01/31 |  | History parameters | R | WORD (BitString16) | -
DCC0 | Command channel | 16#FB2C = 64300 |  |  | CNL | History parameters | R | WORD (Enumeration) | -
RTP0 | Run Elapsed time | 16#1C5C = 7260 | 16#202A/3D | 16#85/01/3D = 133/01/61 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h
OTP0 | Motor torque | 16#1CA2 = 7330 | 16#202B/1F | 16#85/01/83 = 133/01/131 |  | History parameters | R | INT (Signed16) | 1 % |  | -32767 % ... 32767 %
TSP0 | Device thermal state | 16#1CCA = 7370 | 16#202B/47 | 16#85/01/AB = 133/01/171 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 200 %
AGP0 | Warning group status | 16#1E5A = 7770 | 16#202F/47 | 16#87/01/AB = 135/01/171 |  | History parameters | R | WORD (BitString16) | -
DP1 | Fault code on fault n-1 | 16#1C21 = 7201 | 16#202A/2 | 16#85/01/02 = 133/01/02 | LFT | History parameters | R | WORD (Enumeration) | -
LCP1 | Motor current | 16#1C49 = 7241 | 16#202A/2A | 16#85/01/2A = 133/01/42 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCP1) | [None] (DP1)
THP1 | Motor thermal state | 16#1C71 = 7281 | 16#202A/52 | 16#85/01/52 = 133/01/82 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THP1) | [None] (DP1)
EP1 | Status of last error 1 | 16#1C2B = 7211 | 16#202A/C | 16#85/01/0C = 133/01/12 |  | History parameters | R | WORD (BitString16) | - |  |  | [Last Error 1 Status] (EP1) | [None] (DP1)
IP1 | ETI state word | 16#1C35 = 7221 | 16#202A/16 | 16#85/01/16 = 133/01/22 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP1) | [None] (DP1)
CMP1 | Cmd word | 16#1C3F = 7231 | 16#202A/20 | 16#85/01/20 = 133/01/32 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP1) | [None] (DP1)
DCC1 | Command channel | 16#FB2D = 64301 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC1) | [None] (DP1)
RTP1 | Run Elapsed time | 16#1C5D = 7261 | 16#202A/3E | 16#85/01/3E = 133/01/62 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTP1) | [None] (DP1)
OTP1 | Motor torque | 16#1CA3 = 7331 | 16#202B/20 | 16#85/01/84 = 133/01/132 |  | History parameters | R | INT (Signed16) | 1 % |  | -32767 % ... 32767 % | [Motor Torque] (OTP1) | [None] (DP1)
TSP1 | Device thermal state | 16#1CCB = 7371 | 16#202B/48 | 16#85/01/AC = 133/01/172 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 200 % | [Device Thermal State] (TSP1) | [None] (DP1)
AGP1 | Warning group status | 16#1E5B = 7771 | 16#202F/48 | 16#87/01/AC = 135/01/172 |  | History parameters | R | WORD (BitString16) | - |  |  | [Warn Group Status] (AGP1) | [None] (DP1)
DP2 | Fault code on fault n-2 | 16#1C22 = 7202 | 16#202A/3 | 16#85/01/03 = 133/01/03 | LFT | History parameters | R | WORD (Enumeration) | -
LCP2 | Motor current | 16#1C4A = 7242 | 16#202A/2B | 16#85/01/2B = 133/01/43 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCP2) | [None] (DP2)
THP2 | Motor thermal state | 16#1C72 = 7282 | 16#202A/53 | 16#85/01/53 = 133/01/83 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THP2) | [None] (DP2)
EP2 | Status of last error 2 | 16#1C2C = 7212 | 16#202A/D | 16#85/01/0D = 133/01/13 |  | History parameters | R | WORD (BitString16) | - |  |  | [Last Error 2 Status] (EP2) | [None] (DP2)
IP2 | ETI state word | 16#1C36 = 7222 | 16#202A/17 | 16#85/01/17 = 133/01/23 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP2) | [None] (DP2)
CMP2 | Cmd word | 16#1C40 = 7232 | 16#202A/21 | 16#85/01/21 = 133/01/33 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP2) | [None] (DP2)
DCC2 | Command channel | 16#FB2E = 64302 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC2) | [None] (DP2)
RTP2 | Run Elapsed time | 16#1C5E = 7262 | 16#202A/3F | 16#85/01/3F = 133/01/63 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTP2) | [None] (DP2)
OTP2 | Motor torque | 16#1CA4 = 7332 | 16#202B/21 | 16#85/01/85 = 133/01/133 |  | History parameters | R | INT (Signed16) | 1 % |  | -32767 % ... 32767 % | [Motor Torque] (OTP2) | [None] (DP2)
TSP2 | Device thermal state | 16#1CCC = 7372 | 16#202B/49 | 16#85/01/AD = 133/01/173 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 200 % | [Device Thermal State] (TSP2) | [None] (DP2)
AGP2 | Warning group status | 16#1E5C = 7772 | 16#202F/49 | 16#87/01/AD = 135/01/173 |  | History parameters | R | WORD (BitString16) | - |  |  | [Warn Group Status] (AGP2) | [None] (DP2)
DP3 | Fault code on fault n-3 | 16#1C23 = 7203 | 16#202A/4 | 16#85/01/04 = 133/01/04 | LFT | History parameters | R | WORD (Enumeration) | -
LCP3 | Motor current | 16#1C4B = 7243 | 16#202A/2C | 16#85/01/2C = 133/01/44 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCP3) | [None] (DP3)
THP3 | Motor thermal state | 16#1C73 = 7283 | 16#202A/54 | 16#85/01/54 = 133/01/84 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THP3) | [None] (DP3)
EP3 | Status of last error 3 | 16#1C2D = 7213 | 16#202A/E | 16#85/01/0E = 133/01/14 |  | History parameters | R | WORD (BitString16) | - |  |  | [Last Error 3 Status] (EP3) | [None] (DP3)
IP3 | ETI state word | 16#1C37 = 7223 | 16#202A/18 | 16#85/01/18 = 133/01/24 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP3) | [None] (DP3)
CMP3 | Cmd word | 16#1C41 = 7233 | 16#202A/22 | 16#85/01/22 = 133/01/34 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP3) | [None] (DP3)
DCC3 | Command channel | 16#FB2F = 64303 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC3) | [None] (DP3)
RTP3 | Run Elapsed time | 16#1C5F = 7263 | 16#202A/40 | 16#85/01/40 = 133/01/64 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTP3) | [None] (DP3)
OTP3 | Motor torque | 16#1CA5 = 7333 | 16#202B/22 | 16#85/01/86 = 133/01/134 |  | History parameters | R | INT (Signed16) | 1 % |  | -32767 % ... 32767 % | [Motor Torque] (OTP3) | [None] (DP3)
TSP3 | Device thermal state | 16#1CCD = 7373 | 16#202B/4A | 16#85/01/AE = 133/01/174 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 200 % | [Device Thermal State] (TSP3) | [None] (DP3)
AGP3 | Warning group status | 16#1E5D = 7773 | 16#202F/4A | 16#87/01/AE = 135/01/174 |  | History parameters | R | WORD (BitString16) | - |  |  | [Warn Group Status] (AGP3) | [None] (DP3)
DP4 | Fault code on fault n-4 | 16#1C24 = 7204 | 16#202A/5 | 16#85/01/05 = 133/01/05 | LFT | History parameters | R | WORD (Enumeration) | -
LCP4 | Motor current | 16#1C4C = 7244 | 16#202A/2D | 16#85/01/2D = 133/01/45 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCP4) | [None] (DP4)
THP4 | Motor thermal state | 16#1C74 = 7284 | 16#202A/55 | 16#85/01/55 = 133/01/85 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THP4) | [None] (DP4)
EP4 | Status of last error 4 | 16#1C2E = 7214 | 16#202A/F | 16#85/01/0F = 133/01/15 |  | History parameters | R | WORD (BitString16) | - |  |  | [Last Error 4 Status] (EP4) | [None] (DP4)
IP4 | ETI state word | 16#1C38 = 7224 | 16#202A/19 | 16#85/01/19 = 133/01/25 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP4) | [None] (DP4)
CMP4 | Cmd word | 16#1C42 = 7234 | 16#202A/23 | 16#85/01/23 = 133/01/35 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP4) | [None] (DP4)
DCC4 | Command channel | 16#FB30 = 64304 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC4) | [None] (DP4)
RTP4 | Run Elapsed time | 16#1C60 = 7264 | 16#202A/41 | 16#85/01/41 = 133/01/65 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTP4) | [None] (DP4)
OTP4 | Motor torque | 16#1CA6 = 7334 | 16#202B/23 | 16#85/01/87 = 133/01/135 |  | History parameters | R | INT (Signed16) | 1 % |  | -32767 % ... 32767 % | [Motor Torque] (OTP4) | [None] (DP4)
TSP4 | Device thermal state | 16#1CCE = 7374 | 16#202B/4B | 16#85/01/AF = 133/01/175 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 200 % | [Device Thermal State] (TSP4) | [None] (DP4)
AGP4 | Warning group status | 16#1E5E = 7774 | 16#202F/4B | 16#87/01/AF = 135/01/175 |  | History parameters | R | WORD (BitString16) | - |  |  | [Warn Group Status] (AGP4) | [None] (DP4)
DP5 | Fault code on fault n-5 | 16#1C25 = 7205 | 16#202A/6 | 16#85/01/06 = 133/01/06 | LFT | History parameters | R | WORD (Enumeration) | -
LCP5 | Motor current | 16#1C4D = 7245 | 16#202A/2E | 16#85/01/2E = 133/01/46 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCP5) | [None] (DP5)
THP5 | Motor thermal state | 16#1C75 = 7285 | 16#202A/56 | 16#85/01/56 = 133/01/86 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THP5) | [None] (DP5)
EP5 | State word | 16#1C2F = 7215 | 16#202A/10 | 16#85/01/10 = 133/01/16 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (EP5) | [None] (DP5)
IP5 | ETI state word | 16#1C39 = 7225 | 16#202A/1A | 16#85/01/1A = 133/01/26 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP5) | [None] (DP5)
CMP5 | Cmd word | 16#1C43 = 7235 | 16#202A/24 | 16#85/01/24 = 133/01/36 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP5) | [None] (DP5)
DCC5 | Command channel | 16#FB31 = 64305 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC5) | [None] (DP5)
RTP5 | Run Elapsed time | 16#1C61 = 7265 | 16#202A/42 | 16#85/01/42 = 133/01/66 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTP5) | [None] (DP5)
OTP5 | Motor torque | 16#1CA7 = 7335 | 16#202B/24 | 16#85/01/88 = 133/01/136 |  | History parameters | R | INT (Signed16) | 1 % |  | -32767 % ... 32767 % | [Motor Torque] (OTP5) | [None] (DP5)
TSP5 | Device thermal state | 16#1CCF = 7375 | 16#202B/4C | 16#85/01/B0 = 133/01/176 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 200 % | [Device Thermal State] (TSP5) | [None] (DP5)
AGP5 | Warning group status | 16#1E5F = 7775 | 16#202F/4C | 16#87/01/B0 = 135/01/176 |  | History parameters | R | WORD (BitString16) | - |  |  | [Warn Group Status] (AGP5) | [None] (DP5)
DP6 | Fault code on fault n-6 | 16#1C26 = 7206 | 16#202A/7 | 16#85/01/07 = 133/01/07 | LFT | History parameters | R | WORD (Enumeration) | -
LCP6 | Motor current | 16#1C4E = 7246 | 16#202A/2F | 16#85/01/2F = 133/01/47 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCP6) | [None] (DP6)
THP6 | Motor thermal state | 16#1C76 = 7286 | 16#202A/57 | 16#85/01/57 = 133/01/87 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THP6) | [None] (DP6)
EP6 | State word | 16#1C30 = 7216 | 16#202A/11 | 16#85/01/11 = 133/01/17 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (EP6) | [None] (DP6)
IP6 | ETI state word | 16#1C3A = 7226 | 16#202A/1B | 16#85/01/1B = 133/01/27 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP6) | [None] (DP6)
CMP6 | Cmd word | 16#1C44 = 7236 | 16#202A/25 | 16#85/01/25 = 133/01/37 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP6) | [None] (DP6)
DCC6 | Command channel | 16#FB32 = 64306 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC6) | [None] (DP6)
RTP6 | Run Elapsed time | 16#1C62 = 7266 | 16#202A/43 | 16#85/01/43 = 133/01/67 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTP6) | [None] (DP6)
OTP6 | Motor torque | 16#1CA8 = 7336 | 16#202B/25 | 16#85/01/89 = 133/01/137 |  | History parameters | R | INT (Signed16) | 1 % |  | -32767 % ... 32767 % | [Motor Torque] (OTP6) | [None] (DP6)
TSP6 | Device thermal state | 16#1CD0 = 7376 | 16#202B/4D | 16#85/01/B1 = 133/01/177 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 200 % | [Device Thermal State] (TSP6) | [None] (DP6)
AGP6 | Warning group status | 16#1E60 = 7776 | 16#202F/4D | 16#87/01/B1 = 135/01/177 |  | History parameters | R | WORD (BitString16) | - |  |  | [Warn Group Status] (AGP6) | [None] (DP6)
DP7 | Fault code on fault n-7 | 16#1C27 = 7207 | 16#202A/8 | 16#85/01/08 = 133/01/08 | LFT | History parameters | R | WORD (Enumeration) | -
LCP7 | Motor current | 16#1C4F = 7247 | 16#202A/30 | 16#85/01/30 = 133/01/48 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCP7) | [None] (DP7)
THP7 | Motor thermal state | 16#1C77 = 7287 | 16#202A/58 | 16#85/01/58 = 133/01/88 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THP7) | [None] (DP7)
EP7 | State word | 16#1C31 = 7217 | 16#202A/12 | 16#85/01/12 = 133/01/18 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (EP7) | [None] (DP7)
IP7 | ETI state word | 16#1C3B = 7227 | 16#202A/1C | 16#85/01/1C = 133/01/28 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP7) | [None] (DP7)
CMP7 | Cmd word | 16#1C45 = 7237 | 16#202A/26 | 16#85/01/26 = 133/01/38 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP7) | [None] (DP7)
DCC7 | Command channel | 16#FB33 = 64307 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC7) | [None] (DP7)
RTP7 | Run Elapsed time | 16#1C63 = 7267 | 16#202A/44 | 16#85/01/44 = 133/01/68 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTP7) | [None] (DP7)
OTP7 | Motor torque | 16#1CA9 = 7337 | 16#202B/26 | 16#85/01/8A = 133/01/138 |  | History parameters | R | INT (Signed16) | 1 % |  | -32767 % ... 32767 % | [Motor Torque] (OTP7) | [None] (DP7)
TSP7 | Device thermal state | 16#1CD1 = 7377 | 16#202B/4E | 16#85/01/B2 = 133/01/178 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 200 % | [Device Thermal State] (TSP7) | [None] (DP7)
AGP7 | Warning group status | 16#1E61 = 7777 | 16#202F/4E | 16#87/01/B2 = 135/01/178 |  | History parameters | R | WORD (BitString16) | - |  |  | [Warn Group Status] (AGP7) | [None] (DP7)
DP8 | Fault code on fault n-8 | 16#1C28 = 7208 | 16#202A/9 | 16#85/01/09 = 133/01/09 | LFT | History parameters | R | WORD (Enumeration) | -
LCP8 | Motor current | 16#1C50 = 7248 | 16#202A/31 | 16#85/01/31 = 133/01/49 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCP8) | [None] (DP8)
THP8 | Motor thermal state | 16#1C78 = 7288 | 16#202A/59 | 16#85/01/59 = 133/01/89 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THP8) | [None] (DP8)
EP8 | State word | 16#1C32 = 7218 | 16#202A/13 | 16#85/01/13 = 133/01/19 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (EP8) | [None] (DP8)
IP8 | ETI state word | 16#1C3C = 7228 | 16#202A/1D | 16#85/01/1D = 133/01/29 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP8) | [None] (DP8)
CMP8 | Cmd word | 16#1C46 = 7238 | 16#202A/27 | 16#85/01/27 = 133/01/39 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP8) | [None] (DP8)
DCC8 | Command channel | 16#FB34 = 64308 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC8) | [None] (DP8)
RTP8 | Run Elapsed time | 16#1C64 = 7268 | 16#202A/45 | 16#85/01/45 = 133/01/69 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTP8) | [None] (DP8)
OTP8 | Motor torque | 16#1CAA = 7338 | 16#202B/27 | 16#85/01/8B = 133/01/139 |  | History parameters | R | INT (Signed16) | 1 % |  | -32767 % ... 32767 % | [Motor Torque] (OTP8) | [None] (DP8)
TSP8 | Device thermal state | 16#1CD2 = 7378 | 16#202B/4F | 16#85/01/B3 = 133/01/179 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 200 % | [Device Thermal State] (TSP8) | [None] (DP8)
AGP8 | Warning group status | 16#1E62 = 7778 | 16#202F/4F | 16#87/01/B3 = 135/01/179 |  | History parameters | R | WORD (BitString16) | - |  |  | [Warn Group Status] (AGP8) | [None] (DP8)
VDP | Device software version | 16#0CE6 = 3302 | 16#2003/3 | 16#71/01/67 = 113/01/103 |  | Identification parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
NCD | Product current rating | 16#0C0A = 3082 | 16#2000/53 | 16#70/01/53 = 112/01/83 | NCD | Identification parameters | R | WORD (Enumeration) | - | [Unknown rating] UNK |  | [Product Rating] (NCD) | [Simulation mode] (SIMU)
SCAL | Product voltage range | 16#0C09 = 3081 | 16#2000/52 | 16#70/01/52 = 112/01/82 | SCAL | Identification parameters | R | WORD (Enumeration) | - | [Unknown range] UNK
ICL | Rating | 16#0C08 = 3080 | 16#2000/51 | 16#70/01/51 = 112/01/81 |  | Identification parameters | R | UINT (Unsigned16) | 0.1 A | Refer to programming manual | 0.0 A ... 1200.0 A
NC1 | Com scan output 1 value | 16#31D9 = 12761 | 16#2061/3E | 16#A0/01/A2 = 160/01/162 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out1 val.] (NC1) | [Com scan output map] (OSA)
NC2 | Com scan output 2 value | 16#31DA = 12762 | 16#2061/3F | 16#A0/01/A3 = 160/01/163 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out2 val.] (NC2) | [Com scan output map] (OSA)
NC3 | Com scan output 3 value | 16#31DB = 12763 | 16#2061/40 | 16#A0/01/A4 = 160/01/164 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out3 val.] (NC3) | [Com scan output map] (OSA)
NC4 | Com scan output 4 value | 16#31DC = 12764 | 16#2061/41 | 16#A0/01/A5 = 160/01/165 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out4 val.] (NC4) | [Com scan output map] (OSA)
NC5 | Com scan output 5 value | 16#31DD = 12765 | 16#2061/42 | 16#A0/01/A6 = 160/01/166 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out5 val.] (NC5) | [Com scan output map] (OSA)
NC6 | Com scan output 6 value | 16#31DE = 12766 | 16#2061/43 | 16#A0/01/A7 = 160/01/167 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out6 val.] (NC6) | [Com scan output map] (OSA)
NC7 | Com scan output 7 value | 16#31DF = 12767 | 16#2061/44 | 16#A0/01/A8 = 160/01/168 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out7 val.] (NC7) | [Com scan output map] (OSA)
NC8 | Com scan output 8 value | 16#31E0 = 12768 | 16#2061/45 | 16#A0/01/A9 = 160/01/169 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out8 val.] (NC8) | [Com scan output map] (OSA)
NM1 | Com scan input 1 value | 16#31C5 = 12741 | 16#2061/2A | 16#A0/01/8E = 160/01/142 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In1 val.] (NM1) | [Com. scanner input map] (ISA)
NM2 | Com scan input 2 value | 16#31C6 = 12742 | 16#2061/2B | 16#A0/01/8F = 160/01/143 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In2 val.] (NM2) | [Com. scanner input map] (ISA)
NM3 | Com scan input 3 value | 16#31C7 = 12743 | 16#2061/2C | 16#A0/01/90 = 160/01/144 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In3 val.] (NM3) | [Com. scanner input map] (ISA)
NM4 | Com scan input 4 value | 16#31C8 = 12744 | 16#2061/2D | 16#A0/01/91 = 160/01/145 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In4 val.] (NM4) | [Com. scanner input map] (ISA)
NM5 | Com scan input 5 value | 16#31C9 = 12745 | 16#2061/2E | 16#A0/01/92 = 160/01/146 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In5 val.] (NM5) | [Com. scanner input map] (ISA)
NM6 | Com scan input 6 value | 16#31CA = 12746 | 16#2061/2F | 16#A0/01/93 = 160/01/147 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In6 val.] (NM6) | [Com. scanner input map] (ISA)
NM7 | Com scan input 7 value | 16#31CB = 12747 | 16#2061/30 | 16#A0/01/94 = 160/01/148 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In7 val.] (NM7) | [Com. scanner input map] (ISA)
NM8 | Com scan input 8 value | 16#31CC = 12748 | 16#2061/31 | 16#A0/01/95 = 160/01/149 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In8 val.] (NM8) | [Com. scanner input map] (ISA)
SCS | Save configuration | 16#1F41 = 8001 | 16#2032/2 | 16#89/01/02 = 137/01/02 | SCS | Configuration management | R/WS | WORD (Enumeration) | - | [No] NO
FCS | Restore configuration | 16#1F42 = 8002 | 16#2032/3 | 16#89/01/03 = 137/01/03 | FCS | Configuration management | R/WS | WORD (Enumeration) | - | [No] NO
FRY | Factory setting group | 16#0BCE = 3022 | 16#2000/17 | 16#70/01/17 = 112/01/23 |  | Configuration management | R/WS | WORD (BitString16) | - | BIT1
AI1T | Configuration of AI1 | 16#1137 = 4407 | 16#200E/8 | 16#77/01/08 = 119/01/08 | AIOT | Configuration and settings | R/WS | WORD (Enumeration) | - | [PTC] PTC |  | [AI1 Type] (AI1T) | [Thermal monitoring] (TPP) [AI1 configuration] (AI1)
AI1F | AI1 filter | 16#1164 = 4452 | 16#200E/35 | 16#77/01/35 = 119/01/53 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 10.00 s | [AI1 filter] (AI1F) | [Thermal monitoring] (TPP) [AI1 configuration] (AI1) [AI1] (AI1C)
AO1 | AQ1 assignment | 16#139D = 5021 | 16#2014/16 | 16#7A/01/16 = 122/01/22 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Motor current] OCR |  | [AQ1 assignment] (AO1) | [AQ1 configuration] (AO1) [AQ1] (AO1C)
AO1T | AQ1 Type | 16#11F9 = 4601 | 16#2010/2 | 16#78/01/02 = 120/01/02 | AIOT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Current] 0A |  | [AQ1 Type] (AO1T) | [AQ1 configuration] (AO1)
AOL1 | AQ1 min output value | 16#1221 = 4641 | 16#2010/2A | 16#78/01/2A = 120/01/42 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 0.0 mA | 0.0 mA ... 20.0 mA | [AQ1 min output] (AOL1) | [AQ1 configuration] (AO1) [AQ1] (AO1C)
AOH1 | AQ1 max output value | 16#122B = 4651 | 16#2010/34 | 16#78/01/34 = 120/01/52 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 20.0 mA | 0.0 mA ... 20.0 mA | [AQ1 max output] (AOH1) | [AQ1 configuration] (AO1) [AQ1] (AO1C)
UOL1 | AQ1 minimum output | 16#120D = 4621 | 16#2010/16 | 16#78/01/16 = 120/01/22 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 0.0 V | 0.0 V ... 10.0 V | [AQ1 min Output] (UOL1) | [AQ1 configuration] (AO1) [AQ1] (AO1C)
UOH1 | AQ1 maximum output | 16#1217 = 4631 | 16#2010/20 | 16#78/01/20 = 120/01/32 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 10.0 V | 0.0 V ... 10.0 V | [AQ1 max Output] (UOH1) | [AQ1 configuration] (AO1) [AQ1] (AO1C)
ASL1 | Scaling AQ1 min | 16#1235 = 4661 | 16#2010/3E | 16#78/01/3E = 120/01/62 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 % | 0.0 % | 0.0 % ... 100.0 % | [Scaling AQ1 min] (ASL1) | [AQ1 configuration] (AO1) [AQ1] (AO1C)
ASH1 | Scaling AQ1 max | 16#123F = 4671 | 16#2010/48 | 16#78/01/48 = 120/01/72 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 % | 100.0 % | 0.0 % ... 100.0 % | [Scaling AQ1 max] (ASH1) | [AQ1 configuration] (AO1) [AQ1] (AO1C)
AO1F | AQ1 filter | 16#1203 = 4611 | 16#2010/C | 16#78/01/0C = 120/01/12 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 10.00 s | [AQ1 Filter] (AO1F) | [AQ1 configuration] (AO1) [AQ1] (AO1C)
PST | Stop key enable | 16#FA02 = 64002 |  |  | PST | Configuration and settings | R/WS | WORD (Enumeration) | - | [Stop key priority] YES |  | [Stop Key Enable] (PST) | [Customization] (CUS)
CHCF | Control mode configuration | 16#20D1 = 8401 | 16#2036/2 | 16#8B/01/02 = 139/01/02 | CHCF | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Control Mode] (CHCF) | [Command channel] (CCP)
CCS | Command switching | 16#20E5 = 8421 | 16#2036/16 | 16#8B/01/16 = 139/01/22 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Command channel 1] CD1 |  | [Command Switching] (CCS) | [Command channel] (CCP)
CD1 | Command channel 1 assign | 16#20E7 = 8423 | 16#2036/18 | 16#8B/01/18 = 139/01/24 | CDX | Configuration and settings | R/WS | WORD (Enumeration) | - | [Terminal block] TER |  | [Cmd channel 1] (CD1) | [Command channel] (CCP)
CD2 | Command channel 2 assign | 16#20E8 = 8424 | 16#2036/19 | 16#8B/01/19 = 139/01/25 | CDX | Configuration and settings | R/WS | WORD (Enumeration) | - | [Modbus communication] MDB |  | [Cmd channel 2] (CD2) | [Command channel] (CCP)
COP | Copy Ch.1-Ch.2 | 16#20D2 = 8402 | 16#2036/3 | 16#8B/01/03 = 139/01/03 | COP | Configuration and settings | R/WS | WORD (Enumeration) | - | [No copy] NO |  | [Copy Ch1-Ch2] (COP) | [Command channel] (CCP)
BMP | HMI local/remote command | 16#34D9 = 13529 | 16#2069/1E | 16#A4/01/82 = 164/01/130 | BMP | Configuration and settings | R/WS | WORD (Enumeration) | - | [Disabled] DIS |  | [HMI L/R cmd] (BMP) | [Customization] (CUS)
STT | Type of stop | 16#2BC1 = 11201 | 16#2052/2 | 16#99/01/02 = 153/01/02 | STT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel] F |  | [Type of stop] (STT) | [Simply start] (SIM) [Start & Stop] (SSP)
LLC | Mains contactor control | 16#3522 = 13602 | 16#206A/3 | 16#A5/01/03 = 165/01/03 | CSLOUT | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [Mains Contactor] (LLC) | [Mains contactor command] (LLC)
LES | Device lock assignment | 16#3521 = 13601 | 16#206A/2 | 16#A5/01/02 = 165/01/02 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Device Lock] (LES) | [Mains contactor command] (LLC)
LCT | Time-out after cont. activ. | 16#3523 = 13603 | 16#206A/4 | 16#A5/01/04 = 165/01/04 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 5 s | 1 s ... 999 s | [Mains V. time out] (LCT) | [Mains contactor command] (LLC)
RSF | Fault reset input assignment | 16#1BD4 = 7124 | 16#2029/19 | 16#84/01/7D = 132/01/125 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Fault Reset Assign] (RSF) | [Fault reset] (RST)
RP | Product restart | 16#1BD8 = 7128 | 16#2029/1D | 16#84/01/81 = 132/01/129 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Product restart] (RP) | [Error/Warning handling] (CSWM) [Modbus Fieldbus] (MD1) [Modbus HMI] (MD2) [Eth Module Config] (ETO) [CANopen] (CNO) [Profibus] (PBC) [Device Management] (DMT)
ATR | Automatic fault reset | 16#1BD2 = 7122 | 16#2029/17 | 16#84/01/7B = 132/01/123 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Auto Fault Reset] (ATR) | [Error/Warning handling] (CSWM)
TAR | Fault Reset time | 16#1BD3 = 7123 | 16#2029/18 | 16#84/01/7C = 132/01/124 | DUR | Configuration and settings | R/WS | WORD (Enumeration) | - | [5 minutes] 5 |  | [Fault Reset Time] (TAR) | [Error/Warning handling] (CSWM)
ETF | External error assignment | 16#1BDB = 7131 | 16#2029/20 | 16#84/01/84 = 132/01/132 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Ext Error assign] (ETF) | [External error] (ETF)
INH | Disable error detection | 16#1BD5 = 7125 | 16#2029/1A | 16#84/01/7E = 132/01/126 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Disable Error Detect] (INH) | [Error/Warning handling] (CSWM) [Smoke Extraction] (SMOE)
CLL | Response to Fieldbus module communication interruption | 16#1B67 = 7015 | 16#2028/10 | 16#84/01/10 = 132/01/16 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [Fieldbus Interrupt Resp] (CLL) | [Eth Module Config] (ETO) [Profibus] (PBC)
COL | Response to CANopen error | 16#1B63 = 7011 | 16#2028/C | 16#84/01/0C = 132/01/12 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [CANopen Error Resp] (COL) | [CANopen] (CNO)
SLL | Response to Modbus interruption | 16#1B62 = 7010 | 16#2028/B | 16#84/01/0B = 132/01/11 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [Modbus Error Resp] (SLL) | [Modbus Fieldbus] (MD1)
NCA1 | Scan output 1 address | 16#31B1 = 12721 | 16#2061/16 | 16#A0/01/7A = 160/01/122 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 8501 | 0 ... 65535
NCA2 | Scan output 2 address | 16#31B2 = 12722 | 16#2061/17 | 16#A0/01/7B = 160/01/123 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NCA3 | Scan output 3 address | 16#31B3 = 12723 | 16#2061/18 | 16#A0/01/7C = 160/01/124 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NCA4 | Scan output 4 address | 16#31B4 = 12724 | 16#2061/19 | 16#A0/01/7D = 160/01/125 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NCA5 | Scan output 5 address | 16#31B5 = 12725 | 16#2061/1A | 16#A0/01/7E = 160/01/126 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NCA6 | Scan output 6 address | 16#31B6 = 12726 | 16#2061/1B | 16#A0/01/7F = 160/01/127 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NCA7 | Scan output 7 address | 16#31B7 = 12727 | 16#2061/1C | 16#A0/01/80 = 160/01/128 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NCA8 | Scan output 8 address | 16#31B8 = 12728 | 16#2061/1D | 16#A0/01/81 = 160/01/129 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NMA1 | Scan input 1 address | 16#319D = 12701 | 16#2061/2 | 16#A0/01/66 = 160/01/102 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 3201 | 0 ... 65535
NMA2 | Scan input 2 address | 16#319E = 12702 | 16#2061/3 | 16#A0/01/67 = 160/01/103 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 3204 | 0 ... 65535
NMA3 | Scan input 3 address | 16#319F = 12703 | 16#2061/4 | 16#A0/01/68 = 160/01/104 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 9630 | 0 ... 65535
NMA4 | Scan input 4 address | 16#31A0 = 12704 | 16#2061/5 | 16#A0/01/69 = 160/01/105 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 8606 | 0 ... 65535
NMA5 | Scan input 5 address | 16#31A1 = 12705 | 16#2061/6 | 16#A0/01/6A = 160/01/106 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NMA6 | Scan input 6 address | 16#31A2 = 12706 | 16#2061/7 | 16#A0/01/6B = 160/01/107 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NMA7 | Scan input 7 address | 16#31A3 = 12707 | 16#2061/8 | 16#A0/01/6C = 160/01/108 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NMA8 | Scan input 8 address | 16#31A4 = 12708 | 16#2061/9 | 16#A0/01/6D = 160/01/109 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMA1 | Scan input 1 address | 16#3C29 = 15401 | 16#207C/2 | 16#AE/01/02 = 174/01/02 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 3201 | 0 ... 65535
OMA2 | Scan input 2 address | 16#3C2A = 15402 | 16#207C/3 | 16#AE/01/03 = 174/01/03 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 3204 | 0 ... 65535
OMA3 | Scan input 3 address | 16#3C2B = 15403 | 16#207C/4 | 16#AE/01/04 = 174/01/04 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 9630 | 0 ... 65535
OMA4 | Scan input 4 address | 16#3C2C = 15404 | 16#207C/5 | 16#AE/01/05 = 174/01/05 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 8606 | 0 ... 65535
OMA5 | Scan input 5 address | 16#3C2D = 15405 | 16#207C/6 | 16#AE/01/06 = 174/01/06 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMA6 | Scan input 6 address | 16#3C2E = 15406 | 16#207C/7 | 16#AE/01/07 = 174/01/07 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCA1 | Scan output 1 address | 16#3C3D = 15421 | 16#207C/16 | 16#AE/01/16 = 174/01/22 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 8501 | 0 ... 65535
OCA2 | Scan output 2 address | 16#3C3E = 15422 | 16#207C/17 | 16#AE/01/17 = 174/01/23 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCA3 | Scan output 3 address | 16#3C3F = 15423 | 16#207C/18 | 16#AE/01/18 = 174/01/24 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCA4 | Scan output 4 address | 16#3C40 = 15424 | 16#207C/19 | 16#AE/01/19 = 174/01/25 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCA5 | Scan output 5 address | 16#3C41 = 15425 | 16#207C/1A | 16#AE/01/1A = 174/01/26 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCA6 | Scan output 6 address | 16#3C42 = 15426 | 16#207C/1B | 16#AE/01/1B = 174/01/27 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
ADD | Device modbus address | 16#1771 = 6001 | 16#201E/2 | 16#7F/01/02 = 127/01/02 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 247 | [Modbus Address] (ADD) | [Modbus Fieldbus] (MD1)
TBR | Modbus baud rate | 16#1773 = 6003 | 16#201E/4 | 16#7F/01/04 = 127/01/04 | TBR | Configuration and settings | R/WS | WORD (Enumeration) | - | [19200 bps] 19200 |  | [Modbus Baud Rate] (TBR) | [Modbus Fieldbus] (MD1)
TFO | Modbus format | 16#1774 = 6004 | 16#201E/5 | 16#7F/01/05 = 127/01/05 | FOR | Configuration and settings | R/WS | WORD (Enumeration) | - | [8 bits even parity 1 stop bit] 8E1 |  | [Modbus Format] (TFO) | [Modbus Fieldbus] (MD1)
TTO | Modbus timeout | 16#1775 = 6005 | 16#201E/6 | 16#7F/01/06 = 127/01/06 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 5.0 s | 0.1 s ... 30.0 s | [ModbusTimeout] (TTO) | [Modbus Fieldbus] (MD1)
ADCO | Device CANopen address | 16#17A3 = 6051 | 16#201E/34 | 16#7F/01/34 = 127/01/52 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 127 | [CANopen Address] (ADCO) | [CANopen] (CNO)
BDCO | CANopen baudrate | 16#17A5 = 6053 | 16#201E/36 | 16#7F/01/36 = 127/01/54 | BDCO | Configuration and settings | R/WS | WORD (Enumeration) | - | [Baud rate 250kbps] 250K |  | [CANopen Baudrate] (BDCO) | [CANopen] (CNO)
ERCO | CANopen error | 16#17A8 = 6056 | 16#201E/39 | 16#7F/01/39 = 127/01/57 |  | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 5 | [CANopen Error] (ERCO) | [CANopen map] (CNM)
FLO | Forced local assignment | 16#20EF = 8431 | 16#2036/20 | 16#8B/01/20 = 139/01/32 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Digital input 4] LI4 |  | [Forced Local Assign] (FLO) | [Command channel] (CCP)
FLOC | Forced Local channel assignment | 16#20F0 = 8432 | 16#2036/21 | 16#8B/01/21 = 139/01/33 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Forced Local Chan] (FLOC) | [Command channel] (CCP)
FLOT | Time-out forc. local | 16#20F1 = 8433 | 16#2036/22 | 16#8B/01/22 = 139/01/34 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 10.0 s | 0.1 s ... 30.0 s | [Time-out forc. local] (FLOT) | [Command channel] (CCP)
ADRC | Device address | 16#19C9 = 6601 | 16#2024/2 | 16#82/01/02 = 130/01/02 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | Refer to programming manual | 0 ... 65535 | [Address] (ADRC) | [Profibus] (PBC)
PRFL | PPO profile used | 16#1A09 = 6665 | 16#2024/42 | 16#82/01/42 = 130/01/66 | PRFL | Configuration and settings | R | WORD (Enumeration) | - | Refer to programming manual |  | [PPO profile used] (PRFL) | [PROFIBUS DIAG] (PRB)
DPMA | DP Master active | 16#1A0A = 6666 | 16#2024/43 | 16#82/01/43 = 130/01/67 | DPMA | Communication parameters | R | WORD (Enumeration) | - | [Master 1] 1 |  | [DP Master Active] (DPMA) | [PROFIBUS DIAG] (PRB)
BDRU | Data rate used | 16#1A04 = 6660 | 16#2024/3D | 16#82/01/3D = 130/01/61 | TBR | Configuration and settings | R | WORD (Enumeration) | - | [Automatic] AUTO |  | [Data rate used] (BDRU) | [PROFIBUS DIAG] (PRB)
ARD | Actual rate and duplex | 16#FB0A = 64266 |  |  | RDS | Configuration and settings | R | WORD (Enumeration) | - |  |  | [Actual rate] (ARD) | [Ethernet Module Diag] (MTE)
L1D | DI1 delay | 16#0FA1 = 4001 | 16#200A/2 | 16#75/01/02 = 117/01/02 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 5 ms | 0 ms ... 200 ms
R1 | R1 assignment | 16#1389 = 5001 | 16#2014/2 | 16#7A/01/02 = 122/01/02 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Device in operating state "Fault"] FLT |  | [R1 Assignment] (R1) | [R1 configuration] (R1)
R2 | R2 assignment | 16#138A = 5002 | 16#2014/3 | 16#7A/01/03 = 122/01/03 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [End of start] BPS
L2D | DI2 delay | 16#0FA2 = 4002 | 16#200A/3 | 16#75/01/03 = 117/01/03 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 5 ms | 0 ms ... 200 ms
R1D | R1 delay time | 16#1091 = 4241 | 16#200C/2A | 16#76/01/2A = 118/01/42 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms
R2D | R2 delay time | 16#1092 = 4242 | 16#200C/2B | 16#76/01/2B = 118/01/43 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms
L3D | DI3 delay | 16#0FA3 = 4003 | 16#200A/4 | 16#75/01/04 = 117/01/04 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 5 ms | 0 ms ... 200 ms
R1S | R1 active level | 16#1069 = 4201 | 16#200C/2 | 16#76/01/02 = 118/01/02 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [High level] POS
R2S | R2 active level | 16#106A = 4202 | 16#200C/3 | 16#76/01/03 = 118/01/03 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [High level] POS
L4D | DI4 delay | 16#0FA4 = 4004 | 16#200A/5 | 16#75/01/05 = 117/01/05 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 5 ms | 0 ms ... 200 ms
R1H | R1 holding time | 16#107D = 4221 | 16#200C/16 | 16#76/01/16 = 118/01/22 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms
R2H | R2 holding time | 16#107E = 4222 | 16#200C/17 | 16#76/01/17 = 118/01/23 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms
DO1 | DQ1 assignment | 16#13A7 = 5031 | 16#2014/20 | 16#7A/01/20 = 122/01/32 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Motor overload warning] OLMA |  | [DQ1 Assignment] (DO1) | [DQ1 configuration] (DO1)
DO2 | DQ2 assignment | 16#13A8 = 5032 | 16#2014/21 | 16#7A/01/21 = 122/01/33 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Device running] RUN |  | [DQ2 Assign] (DO2) | [DQ2 Configuration] (DO2)
DO1D | DQ1 delay time | 16#10B9 = 4281 | 16#200C/52 | 16#76/01/52 = 118/01/82 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms
DO1H | DQ1 holding time | 16#10AF = 4271 | 16#200C/48 | 16#76/01/48 = 118/01/72 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms
DO1S | DQ1 active level | 16#10A5 = 4261 | 16#200C/3E | 16#76/01/3E = 118/01/62 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [High level] POS |  | [DQ1 Active at] (DO1S) | [DQ1 configuration] (DO1)
SAI1 | AI1 physical value without filter | 16#14AB = 5291 | 16#2016/5C | 16#7B/01/5C = 123/01/92 |  | Measurement parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
SAO1 | AO1 physical value without filter | 16#14AF = 5295 | 16#2016/60 | 16#7B/01/60 = 123/01/96 |  | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
ULT | Underload detection delay | 16#384B = 14411 | 16#2072/C | 16#A9/01/0C = 169/01/12 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | Refer to programming manual | 0 s ... 100 s | [Unld Detect Delay] (ULT) | [Process underload] (ULD)
UDL | Response to underload error | 16#384C = 14412 | 16#2072/D | 16#A9/01/0D = 169/01/13 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Underload ErrorResp] (UDL) | [Process underload] (ULD)
TOL | Overload detection delay | 16#3855 = 14421 | 16#2072/16 | 16#A9/01/16 = 169/01/22 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | Refer to programming manual | 0 s ... 100 s | [Ovld Detection Delay] (TOL) | [Process overload] (OLD)
ODL | Response to overload error | 16#3856 = 14422 | 16#2072/17 | 16#A9/01/17 = 169/01/23 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Overload ErrorResp] (ODL) | [Process overload] (OLD)
AI1I | AI1 input physical image (MAX = 8192) | 16#1466 = 5222 | 16#2016/17 | 16#7B/01/17 = 123/01/23 |  | Measurement parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
AO1I | AO1 output physical image (MAX = 8192) | 16#1483 = 5251 | 16#2016/34 | 16#7B/01/34 = 123/01/52 |  | I/O parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
CMP9 | Cmd word | 16#1C47 = 7239 | 16#202A/28 | 16#85/01/28 = 133/01/40 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP9) | [None] (DP9)
CMPA | Cmd word | 16#1DCE = 7630 | 16#202E/1F | 16#87/01/1F = 135/01/31 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMPA) | [None] (DPA)
CMPB | Cmd word | 16#1DCF = 7631 | 16#202E/20 | 16#87/01/20 = 135/01/32 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMPB) | [None] (DPB)
CMPC | CMD command word | 16#1DD0 = 7632 | 16#202E/21 | 16#87/01/21 = 135/01/33 |  | History parameters | R | WORD (BitString16) | - |  |  | [CMD word] (CMPC) | [None] (DPC)
CMPD | CMD command word | 16#1DD1 = 7633 | 16#202E/22 | 16#87/01/22 = 135/01/34 |  | History parameters | R | WORD (BitString16) | - |  |  | [CMD word] (CMPD) | [None] (DPD)
CMPE | CMD command word | 16#1DD2 = 7634 | 16#202E/23 | 16#87/01/23 = 135/01/35 |  | History parameters | R | WORD (BitString16) | - |  |  | [CMD word] (CMPE) | [None] (DPE)
CMPF | CMD command word | 16#1DD3 = 7635 | 16#202E/24 | 16#87/01/24 = 135/01/36 |  | History parameters | R | WORD (BitString16) | - |  |  | [CMD word] (CMPF) | [None] (DPF)
DM0 | Hour and minute of actual fault | 16#1C8E = 7310 | 16#202B/B | 16#85/01/6F = 133/01/111 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DM1 | Hour and minute of fault record x (1 is last) | 16#1C8F = 7311 | 16#202B/C | 16#85/01/70 = 133/01/112 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DM2 | Hour and minute of fault record x (1 is last) | 16#1C90 = 7312 | 16#202B/D | 16#85/01/71 = 133/01/113 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DM3 | Hour and minute of fault record x (1 is last) | 16#1C91 = 7313 | 16#202B/E | 16#85/01/72 = 133/01/114 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DM4 | Hour and minute of fault record x (1 is last) | 16#1C92 = 7314 | 16#202B/F | 16#85/01/73 = 133/01/115 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DM5 | Hour and minute of fault record x (1 is last) | 16#1C93 = 7315 | 16#202B/10 | 16#85/01/74 = 133/01/116 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DM6 | Hour and minute of fault record x (1 is last) | 16#1C94 = 7316 | 16#202B/11 | 16#85/01/75 = 133/01/117 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DM7 | Hour and minute of fault record x (1 is last) | 16#1C95 = 7317 | 16#202B/12 | 16#85/01/76 = 133/01/118 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DM8 | Hour and minute of fault record x (1 is last) | 16#1C96 = 7318 | 16#202B/13 | 16#85/01/77 = 133/01/119 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DM9 | Hour and minute of fault record x (1 is last) | 16#1C97 = 7319 | 16#202B/14 | 16#85/01/78 = 133/01/120 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DMA | Hour and minute of fault record x (1 is last) | 16#1E1E = 7710 | 16#202F/B | 16#87/01/6F = 135/01/111 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DMB | Hour and minute of fault record x (1 is last) | 16#1E1F = 7711 | 16#202F/C | 16#87/01/70 = 135/01/112 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DMC | Hour and minute of fault record x (1 is last) | 16#1E20 = 7712 | 16#202F/D | 16#87/01/71 = 135/01/113 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DMD | Hour and minute of fault record x (1 is last) | 16#1E21 = 7713 | 16#202F/E | 16#87/01/72 = 135/01/114 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DME | Hour and minute of fault record x (1 is last) | 16#1E22 = 7714 | 16#202F/F | 16#87/01/73 = 135/01/115 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DMF | Hour and minute of fault record x (1 is last) | 16#1E23 = 7715 | 16#202F/10 | 16#87/01/74 = 135/01/116 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DP9 | Last error 9 | 16#1C29 = 7209 | 16#202A/A | 16#85/01/0A = 133/01/10 | LFT | History parameters | R | WORD (Enumeration) | -
DPA | Last error 10 | 16#1DB0 = 7600 | 16#202E/1 | 16#87/01/01 = 135/01/01 | LFT | History parameters | R | WORD (Enumeration) | -
DPB | Last error 11 | 16#1DB1 = 7601 | 16#202E/2 | 16#87/01/02 = 135/01/02 | LFT | History parameters | R | WORD (Enumeration) | -
DPC | Last error 12 | 16#1DB2 = 7602 | 16#202E/3 | 16#87/01/03 = 135/01/03 | LFT | History parameters | R | WORD (Enumeration) | -
DPD | Last error 13 | 16#1DB3 = 7603 | 16#202E/4 | 16#87/01/04 = 135/01/04 | LFT | History parameters | R | WORD (Enumeration) | -
DPE | Last error 14 | 16#1DB4 = 7604 | 16#202E/5 | 16#87/01/05 = 135/01/05 | LFT | History parameters | R | WORD (Enumeration) | -
DPF | Last error 15 | 16#1DB5 = 7605 | 16#202E/6 | 16#87/01/06 = 135/01/06 | LFT | History parameters | R | WORD (Enumeration) | -
EP9 | State word | 16#1C33 = 7219 | 16#202A/14 | 16#85/01/14 = 133/01/20 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (EP9) | [None] (DP9)
EPA | State word | 16#1DBA = 7610 | 16#202E/B | 16#87/01/0B = 135/01/11 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (EPA) | [None] (DPA)
EPB | State word | 16#1DBB = 7611 | 16#202E/C | 16#87/01/0C = 135/01/12 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (EPB) | [None] (DPB)
EPC | State word | 16#1DBC = 7612 | 16#202E/D | 16#87/01/0D = 135/01/13 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (EPC) | [None] (DPC)
EPD | State word | 16#1DBD = 7613 | 16#202E/E | 16#87/01/0E = 135/01/14 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (EPD) | [None] (DPD)
EPE | State word | 16#1DBE = 7614 | 16#202E/F | 16#87/01/0F = 135/01/15 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (EPE) | [None] (DPE)
EPF | State word | 16#1DBF = 7615 | 16#202E/10 | 16#87/01/10 = 135/01/16 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (EPF) | [None] (DPF)
EPRW | Active Electrical output power in kW | 16#0CDD = 3293 | 16#2002/5E | 16#71/01/5E = 113/01/94 |  | Actual values parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Acv Elc Out Pwr in kW] (EPRW) | [Motor parameters] (MMO) [Energy parameters] (ENP)
ERR | Ethernet error Code | 16#FB0E = 64270 |  |  |  | Fault parameters | R | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
ETAD | DRIVECOM : Status word | 16#219B = 8603 | 16#2038/4 | 16#8C/01/04 = 140/01/04 |  | Status parameters | R | WORD (BitString16) | -
HS9 | Device state | 16#1CA1 = 7329 | 16#202B/1E | 16#85/01/82 = 133/01/130 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Device state] (HS9) | [None] (DP9)
HSA | Device state | 16#1E28 = 7720 | 16#202F/15 | 16#87/01/79 = 135/01/121 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Device state] (HSA) | [None] (DPA)
HSB | Device state | 16#1E29 = 7721 | 16#202F/16 | 16#87/01/7A = 135/01/122 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Device state] (HSB) | [None] (DPB)
HSC | Device state | 16#1E2A = 7722 | 16#202F/17 | 16#87/01/7B = 135/01/123 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Device state] (HSC) | [None] (DPC)
HSD | Device state | 16#1E2B = 7723 | 16#202F/18 | 16#87/01/7C = 135/01/124 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Device state] (HSD) | [None] (DPD)
HSE | Device state | 16#1E2C = 7724 | 16#202F/19 | 16#87/01/7D = 135/01/125 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Device state] (HSE) | [None] (DPE)
HSF | Device state | 16#1E2D = 7725 | 16#202F/1A | 16#87/01/7E = 135/01/126 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Device state] (HSF) | [None] (DPF)
IL1I | Logic inputs physical image | 16#1451 = 5201 | 16#2016/2 | 16#7B/01/02 = 123/01/02 |  | I/O parameters | R | WORD (BitString16) | -
INRP | NPR power scaling | 16#264A = 9802 | 16#2044/3 | 16#92/01/03 = 146/01/03 | CINR | Configuration and settings | R | WORD (Enumeration) | -
IP9 | ETI state word | 16#1C3D = 7229 | 16#202A/1E | 16#85/01/1E = 133/01/30 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP9) | [None] (DP9)
IPA | ETI state word | 16#1DC4 = 7620 | 16#202E/15 | 16#87/01/15 = 135/01/21 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IPA) | [None] (DPA)
IPB | ETI state word | 16#1DC5 = 7621 | 16#202E/16 | 16#87/01/16 = 135/01/22 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IPB) | [None] (DPB)
IPC | ETI state word | 16#1DC6 = 7622 | 16#202E/17 | 16#87/01/17 = 135/01/23 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IPC) | [None] (DPC)
IPD | ETI state word | 16#1DC7 = 7623 | 16#202E/18 | 16#87/01/18 = 135/01/24 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IPD) | [None] (DPD)
IPE | ETI state word | 16#1DC8 = 7624 | 16#202E/19 | 16#87/01/19 = 135/01/25 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IPE) | [None] (DPE)
IPF | ETI state word | 16#1DC9 = 7625 | 16#202E/1A | 16#87/01/1A = 135/01/26 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IPF) | [None] (DPF)
LALR | Last warning | 16#325A = 12890 | 16#2062/5B | 16#A1/01/5B = 161/01/91 | ALR | Actual values parameters | R | WORD (Enumeration) | - |  |  | [Last Warning] (LALR) | [Diag. data] (DDT)
LCP9 | Motor current | 16#1C51 = 7249 | 16#202A/32 | 16#85/01/32 = 133/01/50 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCP9) | [None] (DP9)
LCPA | Motor current | 16#1DD8 = 7640 | 16#202E/29 | 16#87/01/29 = 135/01/41 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCPA) | [None] (DPA)
LCPB | Motor current | 16#1DD9 = 7641 | 16#202E/2A | 16#87/01/2A = 135/01/42 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCPB) | [None] (DPB)
LCPC | Motor current | 16#1DDA = 7642 | 16#202E/2B | 16#87/01/2B = 135/01/43 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCPC) | [None] (DPC)
LCPD | Motor current | 16#1DDB = 7643 | 16#202E/2C | 16#87/01/2C = 135/01/44 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCPD) | [None] (DPD)
LCPE | Motor current | 16#1DDC = 7644 | 16#202E/2D | 16#87/01/2D = 135/01/45 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCPE) | [None] (DPE)
LCPF | Motor current | 16#1DDD = 7645 | 16#202E/2E | 16#87/01/2E = 135/01/46 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCPF) | [None] (DPF)
LOC | Current overload threshold | 16#3859 = 14425 | 16#2072/1A | 16#A9/01/1A = 169/01/26 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 80 % | 50 % ... 300 % | [Overload Threshold] (LOC) | [Process overload] (OLD)
MD0 | Year, month and day of actual fault | 16#1C84 = 7300 | 16#202B/1 | 16#85/01/65 = 133/01/101 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MD1 | Year, month and day of fault record x (1 is last) | 16#1C85 = 7301 | 16#202B/2 | 16#85/01/66 = 133/01/102 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MD2 | Year, month and day of fault record x (1 is last) | 16#1C86 = 7302 | 16#202B/3 | 16#85/01/67 = 133/01/103 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MD3 | Year, month and day of fault record x (1 is last) | 16#1C87 = 7303 | 16#202B/4 | 16#85/01/68 = 133/01/104 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MD4 | Year, month and day of fault record x (1 is last) | 16#1C88 = 7304 | 16#202B/5 | 16#85/01/69 = 133/01/105 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MD5 | Year, month and day of fault record x (1 is last) | 16#1C89 = 7305 | 16#202B/6 | 16#85/01/6A = 133/01/106 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MD6 | Year, month and day of fault record x (1 is last) | 16#1C8A = 7306 | 16#202B/7 | 16#85/01/6B = 133/01/107 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MD7 | Year, month and day of fault record x (1 is last) | 16#1C8B = 7307 | 16#202B/8 | 16#85/01/6C = 133/01/108 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MD8 | Year, month and day of fault record x (1 is last) | 16#1C8C = 7308 | 16#202B/9 | 16#85/01/6D = 133/01/109 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MD9 | Year, month and day of fault record x (1 is last) | 16#1C8D = 7309 | 16#202B/A | 16#85/01/6E = 133/01/110 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MDA | Year, month and day of fault record x (1 is last) | 16#1E14 = 7700 | 16#202F/1 | 16#87/01/65 = 135/01/101 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MDB | Year, month and day of fault record x (1 is last) | 16#1E15 = 7701 | 16#202F/2 | 16#87/01/66 = 135/01/102 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MDC | Year, month and day of fault record x (1 is last) | 16#1E16 = 7702 | 16#202F/3 | 16#87/01/67 = 135/01/103 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MDD | Year, month and day of fault record x (1 is last) | 16#1E17 = 7703 | 16#202F/4 | 16#87/01/68 = 135/01/104 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MDE | Year, month and day of fault record x (1 is last) | 16#1E18 = 7704 | 16#202F/5 | 16#87/01/69 = 135/01/105 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MDF | Year, month and day of fault record x (1 is last) | 16#1E19 = 7705 | 16#202F/6 | 16#87/01/6A = 135/01/106 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MOEP | Peak output power | 16#2991 = 10641 | 16#204C/2A | 16#96/01/2A = 150/01/42 |  | Status parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Peak Output Power] (MOEP) | [Energy parameters] (ENP)
NSM | Number of motor starts | 16#0CBC = 3260 | 16#2002/3D | 16#71/01/3D = 113/01/61 |  | Configuration and settings | R/WS | UINT (Unsigned32) | 1 |  | 0 ... 4294967295 | [Nb Of Starts] (NSM) | [Counter Management] (ELT)
OC0 | Electrical energy consumed by the motor (Wh) | 16#296E = 10606 | 16#204C/7 | 16#96/01/07 = 150/01/07 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 Wh |  | 0 Wh ... 999 Wh | [Elc Energy Cons] (OC0) | [Energy parameters] (ENP)
OC1 | Electrical energy consumed by the motor (KWh) | 16#296F = 10607 | 16#204C/8 | 16#96/01/08 = 150/01/08 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 kWh |  | 0 kWh ... 999 kWh | [Elc Energy Cons] (OC1) | [Energy parameters] (ENP)
OC2 | Electrical energy consumed by the motor (MWh) | 16#2970 = 10608 | 16#204C/9 | 16#96/01/09 = 150/01/09 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 MWh |  | 0 MWh ... 999 MWh | [Elc Energy Cons] (OC2) | [Energy parameters] (ENP)
OC3 | Electrical energy consumed by the motor (GWh) | 16#2971 = 10609 | 16#204C/A | 16#96/01/0A = 150/01/10 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 GWh |  | 0 GWh ... 999 GWh | [Elc Energy Cons] (OC3) | [Energy parameters] (ENP)
OC4 | Electrical energy consumed by the motor (TWh) | 16#2972 = 10610 | 16#204C/B | 16#96/01/0B = 150/01/11 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 TWh |  | 0 TWh ... 999 TWh | [Elc Energy Cons] (OC4) | [Energy parameters] (ENP)
OCK | Electrical energy consumed by the motor (kWh) | 16#299C = 10652 | 16#204C/35 | 16#96/01/35 = 150/01/53 |  | Actual values parameters | R | UINT (Unsigned32) | 1 kWh |  | 0 kWh ... 4294967295 kWh
OCA7 | Scan output 7 address | 16#3C43 = 15427 | 16#207C/1C | 16#AE/01/1C = 174/01/28 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCA8 | Scan output 8 address | 16#3C44 = 15428 | 16#207C/1D | 16#AE/01/1D = 174/01/29 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCA9 | Scan output 9 address | 16#3C45 = 15429 | 16#207C/1E | 16#AE/01/1E = 174/01/30 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCAA | Scan output 10 address | 16#3C46 = 15430 | 16#207C/1F | 16#AE/01/1F = 174/01/31 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCAB | Scan output 11 address | 16#3C47 = 15431 | 16#207C/20 | 16#AE/01/20 = 174/01/32 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCAC | Scan output 12 address | 16#3C48 = 15432 | 16#207C/21 | 16#AE/01/21 = 174/01/33 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCAD | Scan output 13 address | 16#3C49 = 15433 | 16#207C/22 | 16#AE/01/22 = 174/01/34 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCAE | Scan output 14 address | 16#3C4A = 15434 | 16#207C/23 | 16#AE/01/23 = 174/01/35 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCAF | Scan output 15 address | 16#3C4B = 15435 | 16#207C/24 | 16#AE/01/24 = 174/01/36 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCAG | Scan output 16 address | 16#3C4C = 15436 | 16#207C/25 | 16#AE/01/25 = 174/01/37 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCT | Electrical energy consumed TODAY by the motor (KWh) | 16#297E = 10622 | 16#204C/17 | 16#96/01/17 = 150/01/23 |  | Actual values parameters | R | UINT (Unsigned32) | 1 kWh |  | 0 kWh ... 4294967295 kWh | [Elc Egy Today] (OCT) | [Energy parameters] (ENP)
OCY | Electrical energy consumed YESTERDAY by the motor (KWh) | 16#2980 = 10624 | 16#204C/19 | 16#96/01/19 = 150/01/25 |  | Actual values parameters | R | UINT (Unsigned32) | 1 kWh |  | 0 kWh ... 4294967295 kWh | [Elc Egy Yesterday] (OCY) | [Energy parameters] (ENP)
OMA7 | Scan input 7 address | 16#3C2F = 15407 | 16#207C/8 | 16#AE/01/08 = 174/01/08 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMA8 | Scan input 8 address | 16#3C30 = 15408 | 16#207C/9 | 16#AE/01/09 = 174/01/09 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMA9 | Scan input 9 address | 16#3C31 = 15409 | 16#207C/A | 16#AE/01/0A = 174/01/10 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMAA | Scan input 10 address | 16#3C32 = 15410 | 16#207C/B | 16#AE/01/0B = 174/01/11 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMAB | Scan input 11 address | 16#3C33 = 15411 | 16#207C/C | 16#AE/01/0C = 174/01/12 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMAC | Scan input 12 address | 16#3C34 = 15412 | 16#207C/D | 16#AE/01/0D = 174/01/13 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMAD | Scan input 13 address | 16#3C35 = 15413 | 16#207C/E | 16#AE/01/0E = 174/01/14 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMAE | Scan input 14 address | 16#3C36 = 15414 | 16#207C/F | 16#AE/01/0F = 174/01/15 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMAF | Scan input 15 address | 16#3C37 = 15415 | 16#207C/10 | 16#AE/01/10 = 174/01/16 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMAG | Scan input 16 address | 16#3C38 = 15416 | 16#207C/11 | 16#AE/01/11 = 174/01/17 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OTP9 | Motor torque | 16#1CAB = 7339 | 16#202B/28 | 16#85/01/8C = 133/01/140 |  | History parameters | R | INT (Signed16) | 1 % |  | -32767 % ... 32767 % | [Motor Torque] (OTP9) | [None] (DP9)
OTPA | Motor torque | 16#1E32 = 7730 | 16#202F/1F | 16#87/01/83 = 135/01/131 |  | History parameters | R | INT (Signed16) | 1 % |  | -32767 % ... 32767 % | [Motor Torque] (OTPA) | [None] (DPA)
OTPB | Motor torque | 16#1E33 = 7731 | 16#202F/20 | 16#87/01/84 = 135/01/132 |  | History parameters | R | INT (Signed16) | 1 % |  | -32767 % ... 32767 % | [Motor Torque] (OTPB) | [None] (DPB)
OTPC | Motor torque | 16#1E34 = 7732 | 16#202F/21 | 16#87/01/85 = 135/01/133 |  | History parameters | R | INT (Signed16) | 1 % |  | -32767 % ... 32767 % | [Motor Torque] (OTPC) | [None] (DPC)
OTPD | Motor torque | 16#1E35 = 7733 | 16#202F/22 | 16#87/01/86 = 135/01/134 |  | History parameters | R | INT (Signed16) | 1 % |  | -32767 % ... 32767 % | [Motor Torque] (OTPD) | [None] (DPD)
OTPE | Motor torque | 16#1E36 = 7734 | 16#202F/23 | 16#87/01/87 = 135/01/135 |  | History parameters | R | INT (Signed16) | 1 % |  | -32767 % ... 32767 % | [Motor Torque] (OTPE) | [None] (DPE)
OTPF | Motor torque | 16#1E37 = 7735 | 16#202F/24 | 16#87/01/88 = 135/01/136 |  | History parameters | R | INT (Signed16) | 1 % |  | -32767 % ... 32767 % | [Motor Torque] (OTPF) | [None] (DPF)
PEV1 | TPDO1 Event mask | 16#17B6 = 6070 | 16#201E/47 | 16#7F/01/47 = 127/01/71 |  | Communication parameters | R/WS | WORD (BitString16) | - | 15
PEV2 | TPDO2 Event mask | 16#17B7 = 6071 | 16#201E/48 | 16#7F/01/48 = 127/01/72 |  | Communication parameters | R/WS | WORD (BitString16) | - | 15
PEV3 | TPDO3 Event mask | 16#17B8 = 6072 | 16#201E/49 | 16#7F/01/49 = 127/01/73 |  | Communication parameters | R/WS | WORD (BitString16) | - | 15
PEV4 | TPDO4 Event mask | 16#17B9 = 6073 | 16#201E/4A | 16#7F/01/4A = 127/01/74 |  | Communication parameters | R/WS | WORD (BitString16) | - | 15
R3 | R3 assignment | 16#138B = 5003 | 16#2014/4 | 16#7A/01/04 = 122/01/04 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Device running] RUN |  | [R3 Assignment] (R3) | [R3 configuration] (R3)
R3D | R3 delay time | 16#1093 = 4243 | 16#200C/2C | 16#76/01/2C = 118/01/44 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms
R3H | R3 holding time | 16#107F = 4223 | 16#200C/18 | 16#76/01/18 = 118/01/24 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [R3 Holding time] (R3H) | [R3 configuration] (R3)
R3S | R3 active level | 16#107A = 4218 | 16#200C/13 | 16#76/01/13 = 118/01/19 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [High level] POS |  | [R3 Active at] (R3S) | [R3 configuration] (R3)
RTP9 | Run Elapsed time | 16#1C65 = 7269 | 16#202A/46 | 16#85/01/46 = 133/01/70 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTP9) | [None] (DP9)
RTPA | Run Elapsed time | 16#1DEC = 7660 | 16#202E/3D | 16#87/01/3D = 135/01/61 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTPA) | [None] (DPA)
RTPB | Run Elapsed time | 16#1DED = 7661 | 16#202E/3E | 16#87/01/3E = 135/01/62 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTPB) | [None] (DPB)
RTPC | Run Elapsed time | 16#1DEE = 7662 | 16#202E/3F | 16#87/01/3F = 135/01/63 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTPC) | [None] (DPC)
RTPD | Run Elapsed time | 16#1DEF = 7663 | 16#202E/40 | 16#87/01/40 = 135/01/64 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTPD) | [None] (DPD)
RTPE | Run Elapsed time | 16#1DF0 = 7664 | 16#202E/41 | 16#87/01/41 = 135/01/65 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTPE) | [None] (DPE)
RTPF | Run Elapsed time | 16#1DF1 = 7665 | 16#202E/42 | 16#87/01/42 = 135/01/66 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTPF) | [None] (DPF)
ST02 | Status registers 2 | 16#3EE6 = 16102 | 16#2083/3 | 16#B1/01/67 = 177/01/103 |  | Status parameters | R | WORD (BitString16) | -
ST03 | Status registers 3 | 16#3EE7 = 16103 | 16#2083/4 | 16#B1/01/68 = 177/01/104 |  | Status parameters | R | WORD (BitString16) | -
ST04 | Status registers 4 | 16#3EE8 = 16104 | 16#2083/5 | 16#B1/01/69 = 177/01/105 |  | Status parameters | R | WORD (BitString16) | -
ST05 | Status registers 5 | 16#3EE9 = 16105 | 16#2083/6 | 16#B1/01/6A = 177/01/106 |  | Status parameters | R | WORD (BitString16) | -
ST06 | Status registers 6 | 16#3EEA = 16106 | 16#2083/7 | 16#B1/01/6B = 177/01/107 |  | Status parameters | R | WORD (BitString16) | -
ST07 | Status registers 7 | 16#3EEB = 16107 | 16#2083/8 | 16#B1/01/6C = 177/01/108 |  | Status parameters | R | WORD (BitString16) | -
ST11 | Status registers 11 | 16#3EEF = 16111 | 16#2083/C | 16#B1/01/70 = 177/01/112 |  | Status parameters | R | WORD (BitString16) | -
ST13 | Status registers 13 | 16#3EF1 = 16113 | 16#2083/E | 16#B1/01/72 = 177/01/114 |  | Status parameters | R | WORD (BitString16) | -
ST15 | Status registers 15 | 16#3EF3 = 16115 | 16#2083/10 | 16#B1/01/74 = 177/01/116 |  | Status parameters | R | WORD (BitString16) | -
ST16 | Status registers 16 | 16#3EF4 = 16116 | 16#2083/11 | 16#B1/01/75 = 177/01/117 |  | Status parameters | R | WORD (BitString16) | -
ST17 | Status registers 17 | 16#3EF5 = 16117 | 16#2083/12 | 16#B1/01/76 = 177/01/118 |  | Status parameters | R | WORD (BitString16) | -
TBR2 | Modbus 2 baud rate | 16#1787 = 6023 | 16#201E/18 | 16#7F/01/18 = 127/01/24 | TBR | Configuration and settings | R/WS | WORD (Enumeration) | - | [19200 bps] 19200 |  | [Modbus 2 baud rate] (TBR2) | [Modbus HMI] (MD2)
TFO2 | Modbus 2 format | 16#1788 = 6024 | 16#201E/19 | 16#7F/01/19 = 127/01/25 | FOR | Configuration and settings | R/WS | WORD (Enumeration) | - | [8 bits even parity 1 stop bit] 8E1 |  | [Modbus 2 format] (TFO2) | [Modbus HMI] (MD2)
TH1A | Thermal warning level for AI1 | 16#33A3 = 13219 | 16#2066/14 | 16#A3/01/14 = 163/01/20 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | Refer to programming manual | -32768 ... 32767 | [AI1 Th Warn Level] (TH1A) | [Thermal monitoring] (TPP)
TH1B | Response to thermal error for AI1 | 16#33B7 = 13239 | 16#2066/28 | 16#A3/01/28 = 163/01/40 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [AI1 Th Error Resp] (TH1B) | [Thermal monitoring] (TPP)
TH1F | Thermal error level for AI1 | 16#33AD = 13229 | 16#2066/1E | 16#A3/01/1E = 163/01/30 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | Refer to programming manual | -32768 ... 32767 | [AI1 Th Error Level] (TH1F) | [Thermal monitoring] (TPP)
TH1S | Activation of the thermal monitoring on AI1 | 16#3399 = 13209 | 16#2066/A | 16#A3/01/0A = 163/01/10 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [AI1 Th Monitoring] (TH1S) | [Thermal monitoring] (TPP)
TH1V | AI1 thermal value | 16#33C1 = 13249 | 16#2066/32 | 16#A3/01/32 = 163/01/50 |  | Measurement parameters | R | INT (Signed16) | Refer to programming manual |  | -32768 ... 32767 | [AI1 Th Value] (TH1V) | [Thermal monitoring] (TPP) [Thermal Monitoring] (TPM)
THP9 | Motor thermal state | 16#1C79 = 7289 | 16#202A/5A | 16#85/01/5A = 133/01/90 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THP9) | [None] (DP9)
THPA | Motor thermal state | 16#1E00 = 7680 | 16#202E/51 | 16#87/01/51 = 135/01/81 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THPA) | [None] (DPA)
THPB | Motor thermal state | 16#1E01 = 7681 | 16#202E/52 | 16#87/01/52 = 135/01/82 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THPB) | [None] (DPB)
THPC | Motor thermal state | 16#1E02 = 7682 | 16#202E/53 | 16#87/01/53 = 135/01/83 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THPC) | [None] (DPC)
THPD | Motor thermal state | 16#1E03 = 7683 | 16#202E/54 | 16#87/01/54 = 135/01/84 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THPD) | [None] (DPD)
THPE | Motor thermal state | 16#1E04 = 7684 | 16#202E/55 | 16#87/01/55 = 135/01/85 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THPE) | [None] (DPE)
THPF | Motor thermal state | 16#1E05 = 7685 | 16#202E/56 | 16#87/01/56 = 135/01/86 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THPF) | [None] (DPF)
EPR | Active Electrical output power in % | 16#0CE1 = 3297 | 16#2002/62 | 16#71/01/62 = 113/01/98 |  | Actual values parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 500 % | [Acv Elc Out Pwr in %] (EPR) | [Motor parameters] (MMO)
DCC9 | Command channel | 16#FB4A = 64330 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC9) | [None] (DP9)
DCCA | Command channel | 16#FB4B = 64331 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCCA) | [None] (DPA)
DCCB | Command channel | 16#FB4C = 64332 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCCB) | [None] (DPB)
DCCZ | Command channel | 16#FB4D = 64333 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCCZ) | [None] (DPC)
DCCD | Command channel | 16#FB4E = 64334 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCCD) | [None] (DPD)
DCCE | Command channel | 16#FB4F = 64335 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCCE) | [None] (DPE)
DCCF | Command channel | 16#FB50 = 64336 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCCF) | [None] (DPF)
S_FAC | Mains frequency | 16#35B6 = 13750 | 16#206B/33 | 16#A5/01/97 = 165/01/151 |  | Measurement parameters | R | INT (Signed16) | 0.1 Hz |  | 0.0 Hz ... 100.0 Hz | [Mains Frequency] (S_FAC) | [Motor parameters] (MMO)
INF6 | Internal error 6 (Module identification error) information | 16#1BE1 = 7137 | 16#2029/26 | 16#84/01/8A = 132/01/138 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Error Info (INF6)] (INF6) | [Diag. data] (DDT)
HS1 | HMI status | 16#1C99 = 7321 | 16#202B/16 | 16#85/01/7A = 133/01/122 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Device State] (HS1) | [None] (DP1)
HS2 | HMI status | 16#1C9A = 7322 | 16#202B/17 | 16#85/01/7B = 133/01/123 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Device State] (HS2) | [None] (DP2)
HS3 | HMI status | 16#1C9B = 7323 | 16#202B/18 | 16#85/01/7C = 133/01/124 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Device State] (HS3) | [None] (DP3)
HS4 | HMI status | 16#1C9C = 7324 | 16#202B/19 | 16#85/01/7D = 133/01/125 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Device State] (HS4) | [None] (DP4)
HS5 | HMI status | 16#1C9D = 7325 | 16#202B/1A | 16#85/01/7E = 133/01/126 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Device State] (HS5) | [None] (DP5)
HS6 | HMI status | 16#1C9E = 7326 | 16#202B/1B | 16#85/01/7F = 133/01/127 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Device State] (HS6) | [None] (DP6)
HS7 | HMI status | 16#1C9F = 7327 | 16#202B/1C | 16#85/01/80 = 133/01/128 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Device State] (HS7) | [None] (DP7)
HS8 | HMI status | 16#1CA0 = 7328 | 16#202B/1D | 16#85/01/81 = 133/01/129 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Device State] (HS8) | [None] (DP8)
TWO | Terminal Modbus: Word order | 16#1776 = 6006 | 16#201E/7 | 16#7F/01/07 = 127/01/07 | TWO | Configuration and settings | R/WS | WORD (Enumeration) | - | [Modbus Word Order ON] HIGH |  | [Term word order] (TWO) | [Modbus Fieldbus] (MD1)
TWO2 | Terminal Modbus 2: Word order | 16#178A = 6026 | 16#201E/1B | 16#7F/01/1B = 127/01/27 | TWO | Configuration and settings | R/WS | WORD (Enumeration) | - | [Modbus Word Order ON] HIGH |  | [Term 2 word order] (TWO2) | [Modbus HMI] (MD2)
FDR1 | FDR error status | 16#FBBA = 64442 |  |  | EFDR | Configuration and settings | R | WORD (Enumeration) | - |  |  | [FDR Error Status] (FDR1) | [Fast Device Rep.] (FDRO)
FDS1 | FDR operating state | 16#FBBB = 64443 |  |  | SFDR | Configuration and settings | R | WORD (Enumeration) | - |  |  | [FDR Operating State] (FDS1) | [Fast Device Rep.] (FDRO)
FDA1 | FDR action | 16#FBBC = 64444 |  |  | FDRA | Configuration and settings | R/W | WORD (Enumeration) | - | [NOT ACTIVE] IDLE |  | [FDR Action] (FDA1) | [Fast Device Rep.] (FDRO)
FDV1 | Enable FDR function | 16#FBBD = 64445 |  |  | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Enable FDR] (FDV1) | [Fast Device Rep.] (FDRO)
CIC2 | Incorrect configuration 2 | 16#1C16 = 7190 | 16#2029/5B | 16#84/01/BF = 132/01/191 |  | Fault parameters | R | WORD (BitString16) | -
ILT | Motor limiting current | 16#2698 = 9880 | 16#2044/51 | 16#92/01/51 = 146/01/81 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 400 % | 150 % ... 700 % | [Current Limit] (ILT) | [Simply start] (SIM) [Motor parameters] (MPA)
S_PHE | Detected phase direction | 16#0C4F = 3151 | 16#2001/34 | 16#70/01/98 = 112/01/152 | PHE | Status parameters | R | WORD (Enumeration) | - |  |  | [Phase Direction] (S_PHE) | [Motor parameters] (MMO)
FRC | Mains frequency | 16#0C50 = 3152 | 16#2001/35 | 16#70/01/99 = 112/01/153 | FRC | Configuration and settings | R/WS | WORD (Enumeration) | - | [Auto detection of mains frequency] AUTO |  | [Mains Frequency] (FRC) | [Motor parameters] (MPA)
THP | Motor thermal protection class | 16#2689 = 9865 | 16#2044/42 | 16#92/01/42 = 146/01/66 | THP | Configuration and settings | R/WS | WORD (Enumeration) | - | [Class 10E] 10E |  | [Motor Class] (THP) | [Monitoring] (PROT)
THS | Device thermal state | 16#0FED = 4077 | 16#200A/4E | 16#75/01/4E = 117/01/78 |  | Status parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 200 % | [Device Thermal State] (THS) | [Thermal Monitoring] (TPM)
PHP | Phase loss monitoring | 16#2694 = 9876 | 16#2044/4D | 16#92/01/4D = 146/01/77 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [Yes] YES |  | [Phase Loss Monit] (PHP) | [Monitoring] (PROT)
PHL | Phase loss current threshold | 16#2695 = 9877 | 16#2044/4E | 16#92/01/4E = 146/01/78 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 10 % | 5 % ... 10 % | [Phase Loss Cur Thd] (PHL) | [Monitoring] (PROT)
OCR | Motor current | 16#1324 = 4900 | 16#2013/1 | 16#79/01/65 = 121/01/101 |  | Actual values parameters | R | UINT (Unsigned16) | 0.1 % |  | 0.0 % ... 500.0 % | [Motor Current] (OCR) | [Motor parameters] (MMO)
TSP9 | Device thermal state | 16#1CD3 = 7379 | 16#202B/50 | 16#85/01/B4 = 133/01/180 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 200 % | [Device Thermal State] (TSP9) | [None] (DP9)
AGP9 | Warning group status | 16#1E63 = 7779 | 16#202F/50 | 16#87/01/B4 = 135/01/180 |  | History parameters | R | WORD (BitString16) | - |  |  | [Warn Group Status] (AGP9) | [None] (DP9)
TSPA | Device thermal state | 16#1CD4 = 7380 | 16#202B/51 | 16#85/01/B5 = 133/01/181 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 200 % | [Device Thermal State] (TSPA) | [None] (DPA)
AGPA | Warning group status | 16#1E64 = 7780 | 16#202F/51 | 16#87/01/B5 = 135/01/181 |  | History parameters | R | WORD (BitString16) | - |  |  | [Warn Group Status] (AGPA) | [None] (DPA)
TSPB | Device thermal state | 16#1CD5 = 7381 | 16#202B/52 | 16#85/01/B6 = 133/01/182 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 200 % | [Device Thermal State] (TSPB) | [None] (DPB)
AGPB | Warning group status | 16#1E65 = 7781 | 16#202F/52 | 16#87/01/B6 = 135/01/182 |  | History parameters | R | WORD (BitString16) | - |  |  | [Warn Group Status] (AGPB) | [None] (DPB)
TSPC | Device thermal state | 16#1CD6 = 7382 | 16#202B/53 | 16#85/01/B7 = 133/01/183 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 200 % | [Device Thermal State] (TSPC) | [None] (DPC)
AGPC | Warning group status | 16#1E66 = 7782 | 16#202F/53 | 16#87/01/B7 = 135/01/183 |  | History parameters | R | WORD (BitString16) | - |  |  | [Warn Group Status] (AGPC) | [None] (DPC)
TSPD | Device thermal state | 16#1CD7 = 7383 | 16#202B/54 | 16#85/01/B8 = 133/01/184 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 200 % | [Device Thermal State] (TSPD) | [None] (DPD)
AGPD | Warning group status | 16#1E67 = 7783 | 16#202F/54 | 16#87/01/B8 = 135/01/184 |  | History parameters | R | WORD (BitString16) | - |  |  | [Warn Group Status] (AGPD) | [None] (DPD)
TSPE | Device thermal state | 16#1CD8 = 7384 | 16#202B/55 | 16#85/01/B9 = 133/01/185 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 200 % | [Device Thermal State] (TSPE) | [None] (DPE)
AGPE | Warning group status | 16#1E68 = 7784 | 16#202F/55 | 16#87/01/B9 = 135/01/185 |  | History parameters | R | WORD (BitString16) | - |  |  | [Warn Group Status] (AGPE) | [None] (DPE)
TSPF | Device thermal state | 16#1CD9 = 7385 | 16#202B/56 | 16#85/01/BA = 133/01/186 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 200 % | [Device Thermal State] (TSPF) | [None] (DPF)
AGPF | Warning group status | 16#1E69 = 7785 | 16#202F/56 | 16#87/01/BA = 135/01/186 |  | History parameters | R | WORD (BitString16) | - |  |  | [Warn Group Status] (AGPF) | [None] (DPF)
O_CMD | DRIVECOM control register | 16#0190 = 400 |  |  |  | Compatibility | R/W | WORD (BitString16) | -
O_CMI | Extended control register | 16#0192 = 402 |  |  |  | Compatibility | R/W | WORD (BitString16) | -
O_ETA | DRIVECOM : Status register | 16#0193 = 403 |  |  |  | Compatibility | R | WORD (BitString16) | -
O_ETA2 | DRIVECOM : Status register | 16#01CA = 458 |  |  |  | Compatibility | R | WORD (BitString16) | -
O_ETI | Extended status register | 16#0194 = 404 |  |  |  | Compatibility | R | WORD (BitString16) | -
O_ETI8 | Extended status register | 16#01CB = 459 |  |  |  | Compatibility | R | WORD (BitString16) | -
O_ETI2 | Internal status register 2 | 16#0195 = 405 |  |  |  | Compatibility | R | WORD (BitString16) | -
O_ET28 | Internal status register 2 | 16#01CC = 460 |  |  |  | Compatibility | R | WORD (BitString16) | -
O_ADD | Starter address | 16#08F2 = 2290 |  |  |  | Compatibility | R/WS | UINT (Unsigned16) | 1 |  | 0 ... 247
O_TBR | Baud rate | 16#08F4 = 2292 |  |  | O_TBR | Compatibility | R/WS | WORD (Enumeration) | -
O_FOR | Communication protocol | 16#08F5 = 2293 |  |  | O_FOR | Compatibility | R/WS | WORD (Enumeration) | -
O_TLP | Time-Out | 16#08F7 = 2295 |  |  |  | Compatibility | R/WS | UINT (Unsigned16) | 0.1 s |  | 0.0 s ... 6553.5 s
O_LI3 | Logic Input LI3 assignment | 16#0FB6 = 4022 |  |  | O_LIX | Compatibility | R/WS | WORD (Enumeration) | -
O_LO1 | Logic Output LO1 assignment | 16#0FB7 = 4023 |  |  | O_LOX | Compatibility | R/WS | WORD (Enumeration) | -
O_AO | Analogue output AO assign | 16#0FB8 = 4024 |  |  | O_AO | Compatibility | R/WS | WORD (Enumeration) | -
O_ASC | Analogue output scaling AO | 16#0FB9 = 4025 |  |  |  | Compatibility | R/WS | UINT (Unsigned16) | 1 % |  | 50 % ... 500 %
O_IN | Motor nominal current | 16#0FBA = 4026 |  |  |  | Compatibility | R/WS | UINT (Unsigned16) | 0.1 A |  | 0.1 A ... 6553.5 A
O_LSC | Stator loss compensation | 16#0FBB = 4027 |  |  |  | Compatibility | R/WS | UINT (Unsigned16) | 1 % |  | 0 % ... 90 %
O_BST | Voltage boost level | 16#0FBC = 4028 |  |  |  | Compatibility | R/WS | UINT (Unsigned16) | 1 % |  | 25 % ... 100 %
O_STY | Choice of stop type | 16#0FBD = 4029 |  |  | O_STY | Compatibility | R/WS | WORD (Enumeration) | -
O_PHR | Phase rotation protection | 16#0FBE = 4030 |  |  | O_PHR | Compatibility | R/WS | WORD (Enumeration) | -
O_TBS | Time before starting | 16#0FC0 = 4032 |  |  |  | Compatibility | R/WS | UINT (Unsigned16) | 1 s |  | 0 s ... 999 s
O_TLS | Start too long | 16#0FC1 = 4033 |  |  |  | Compatibility | R/WS | UINT (Unsigned16) | 1 s |  | 0 s ... 999 s
O_THP | Motor thermal protection | 16#0FC2 = 4034 |  |  | O_THP | Compatibility | R/WS | WORD (Enumeration) | -
O_TLI | Torque limit | 16#0FC4 = 4036 |  |  |  | Compatibility | R/WS | UINT (Unsigned16) | 1 % |  | 9 % ... 200 %
O_TQ0 | Initial torque on starting | 16#0FC5 = 4037 |  |  |  | Compatibility | R/WS | UINT (Unsigned16) | 1 % |  | 0 % ... 100 %
O_EDC | Freewheel thr'hld on braking | 16#0FC6 = 4038 |  |  |  | Compatibility | R/WS | UINT (Unsigned16) | 1 % |  | 0 % ... 100 %
O_ILT | Coefficient of current limit | 16#0FC7 = 4039 |  |  |  | Compatibility | R/WS | UINT (Unsigned16) | 1 % |  | 150 % ... 700 %
O_BRC | Int level of braking torque | 16#0FC9 = 4041 |  |  |  | Compatibility | R/WS | UINT (Unsigned16) | 1 % |  | 0 % ... 100 %
O_EBA | Pseudo DC braking level | 16#0FCA = 4042 |  |  |  | Compatibility | R/WS | UINT (Unsigned16) | 1 % |  | 20 % ... 100 %
O_ACC | Acceleration ramp time | 16#0FCB = 4043 |  |  |  | Compatibility | R/WS | UINT (Unsigned16) | 1 s |  | 1 s ... 60 s
O_DEC | Deceleration ramp time | 16#0FCC = 4044 |  |  |  | Compatibility | R/WS | UINT (Unsigned16) | 1 s |  | 1 s ... 60 s
O_IPR | Motor preheat level | 16#0FCD = 4045 |  |  |  | Compatibility | R/WS | UINT (Unsigned16) | 1 % |  | 0 % ... 100 %
O_TPR | Time before preheat | 16#0FCE = 4046 |  |  |  | Compatibility | R/WS | UINT (Unsigned16) | 1 min |  | 0 min ... 999 min
O_TIG | Braking loop gain | 16#0FCF = 4047 |  |  |  | Compatibility | R/WS | UINT (Unsigned16) | 1 % |  | 10 % ... 50 %
O_LI4 | Logic Input LI4 assignment | 16#0FD0 = 4048 |  |  | O_LIX | Compatibility | R/WS | WORD (Enumeration) | -
O_LO2 | Logic Output LO2 assignment | 16#0FD1 = 4049 |  |  | O_LOX | Compatibility | R/WS | WORD (Enumeration) | -
O_R1 | Relay R1 | 16#0FD2 = 4050 |  |  | O_LOX | Compatibility | R/WS | WORD (Enumeration) | -
O_R2 | R2 assignment | 16#0FD3 = 4051 |  |  | O_LOX | Compatibility | R/WS | WORD (Enumeration) | -
O_R3 | Relay R3 assignment | 16#0FD4 = 4052 |  |  | O_LOX | Compatibility | R/WS | WORD (Enumeration) | -
O_0_4 | AO scaling | 16#0FD5 = 4053 |  |  | O_0_4 | Compatibility | R/WS | WORD (Enumeration) | -
O_DLT | Start in delta configuration | 16#0FD6 = 4054 |  |  | O_ONOF | Compatibility | R/WS | WORD (Enumeration) | -
O_ULN | Line Voltage | 16#0FD7 = 4055 |  |  |  | Compatibility | R/WS | UINT (Unsigned16) | 1 V |  | 170 V ... 750 V
O_FRC | Supply frequency | 16#0FD8 = 4056 |  |  | O_FRC | Compatibility | R/WS | WORD (Enumeration) | -
O_SST | Test on low power motor | 16#0FD9 = 4057 |  |  | O_ONOF | Compatibility | R/WS | WORD (Enumeration) | -
O_CSC | Activate cascade function | 16#0FDA = 4058 |  |  | O_ONOF | Compatibility | R/WS | WORD (Enumeration) | -
O_LCR | Motor current | 16#0FDE = 4062 |  |  |  | Compatibility | R | UINT (Unsigned16) | 0.1 A |  | 0.0 A ... 6553.5 A
O_LTR | Motor torque | 16#0FDF = 4063 |  |  |  | Compatibility | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 %
O_THR | Motor thermal state | 16#0FE0 = 4064 |  |  |  | Compatibility | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 %
O_PHE | Phase rotation direction | 16#0FE1 = 4065 |  |  | O_PHE | Compatibility | R | WORD (Enumeration) | -
O_IOL | State of logic I/O | 16#0FE2 = 4066 |  |  |  | Compatibility | R | WORD (BitString16) | -
O_COS | Cosinus phi | 16#0FE3 = 4067 |  |  |  | Compatibility | R | UINT (Unsigned16) | 0.01 |  | 0.00 ... 1.00
O_RNT | Operating time | 16#0FE4 = 4068 |  |  |  | Compatibility | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h
O_AOR | Image of analog output AO | 16#0FE6 = 4070 |  |  |  | Compatibility | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
O_LPR | Active power in % | 16#0FE8 = 4072 |  |  |  | Compatibility | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 %
O_LAP | Active power in kW | 16#0FE9 = 4073 |  |  |  | Compatibility | R | UINT (Unsigned16) | 1 kW |  | 0 kW ... 65535 kW
O_KWH | Power consumption (KWH) | 16#0FEA = 4074 |  |  |  | Compatibility | R | UINT (Unsigned16) | 1 kWh |  | 0 kWh ... 65535 kWh
O_RNTT | Product operating time | 16#0FEB = 4075 |  |  |  | Compatibility | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h
O_ARS | Automatic restart | 16#1004 = 4100 |  |  | O_ONOF | Compatibility | R/WS | WORD (Enumeration) | -
O_PHL | Phase loss level | 16#1005 = 4101 |  |  |  | Compatibility | R/WS | UINT (Unsigned16) | 1 % |  | 5 % ... 10 %
O_PHP | Phase Loss Activation | 16#1006 = 4102 |  |  | O_ONOF | Compatibility | R/WS | WORD (Enumeration) | -
O_ULL | Underload activation | 16#1007 = 4103 |  |  | O_ULL | Compatibility | R/WS | WORD (Enumeration) | -
O_LUL | Underload threshold | 16#1008 = 4104 |  |  |  | Compatibility | R/W | UINT (Unsigned16) | 1 % |  | 0 % ... 100 %
O_TUL | Underload time | 16#1009 = 4105 |  |  |  | Compatibility | R/WS | UINT (Unsigned16) | 1 s |  | 0 s ... 60 s
O_PTC | Activate PTC protection | 16#100A = 4106 |  |  | O_ULL | Compatibility | R/WS | WORD (Enumeration) | -
O_CLP | Torque control | 16#100B = 4107 |  |  | O_ONOF | Compatibility | R/WS | WORD (Enumeration) | -
O_OIL | I overcurrent threshold | 16#100C = 4108 |  |  | O_ULL | Compatibility | R/WS | WORD (Enumeration) | -
O_LOC | Overcurrent level | 16#100D = 4109 |  |  |  | Compatibility | R/W | UINT (Unsigned16) | 1 % |  | 50 % ... 300 %
O_TOL | Overcurrent time | 16#100E = 4110 |  |  |  | Compatibility | R/WS | UINT (Unsigned16) | 0.1 s |  | 0.0 s ... 60.0 s
O_LFT | Last fault which occured | 16#1068 = 4200 |  |  | O_LFT | Compatibility | R | WORD (Enumeration) | -
O_DP1 | Fault record 1 (1 is last) | 16#106B = 4203 |  |  | O_LFT | Compatibility | R | WORD (Enumeration) | -
O_HD1 | Hour and minute of fault record N°1 | 16#106C = 4204 |  |  |  | Compatibility | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
O_EP1 | Status register of fault record 1 (1 is last) | 16#106D = 4205 |  |  |  | Compatibility | R | WORD (BitString16) | -
O_DP2 | Fault record 2 (1 is last) | 16#106E = 4206 |  |  | O_LFT | Compatibility | R | WORD (Enumeration) | -
O_HD2 | Hour and minute of fault record N°2 | 16#106F = 4207 |  |  |  | Compatibility | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
O_EP2 | Status register of fault record 2 (1 is last) | 16#1070 = 4208 |  |  |  | Compatibility | R | WORD (BitString16) | -
O_DP3 | Fault record 3 (1 is last) | 16#1071 = 4209 |  |  | O_LFT | Compatibility | R | WORD (Enumeration) | -
O_HD3 | Hour and minute of fault record N°3 | 16#1072 = 4210 |  |  |  | Compatibility | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
O_EP3 | Status register of fault record 3 (1 is last) | 16#1073 = 4211 |  |  |  | Compatibility | R | WORD (BitString16) | -
O_DP4 | Fault record 4 (1 is last) | 16#1074 = 4212 |  |  | O_LFT | Compatibility | R | WORD (Enumeration) | -
O_HD4 | Hour and minute of fault record N°4 | 16#1075 = 4213 |  |  |  | Compatibility | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
O_EP4 | Status register of fault record 4 (1 is last) | 16#1076 = 4214 |  |  |  | Compatibility | R | WORD (BitString16) | -
O_DP5 | Fault record 5 (1 is last) | 16#1077 = 4215 |  |  | O_LFT | Compatibility | R | WORD (Enumeration) | -
O_HD5 | Hour and minute of fault record N°5 | 16#1078 = 4216 |  |  |  | Compatibility | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
O_EP5 | Status register of fault record 5 (1 is last) | 16#1079 = 4217 |  |  |  | Compatibility | R | WORD (BitString16) | -
O_IN2 | Motor 2 nominal current | 16#10CC = 4300 |  |  |  | Compatibility | R/WS | UINT (Unsigned16) | 0.1 A |  | 0.1 A ... 6553.5 A
O_TL2 | Motor 2 Torque limit | 16#10CD = 4301 |  |  |  | Compatibility | R/WS | UINT (Unsigned16) | 1 % |  | 9 % ... 200 %
O_TQ2 | Motor 2 starting torque | 16#10CE = 4302 |  |  |  | Compatibility | R/WS | UINT (Unsigned16) | 1 % |  | 0 % ... 100 %
O_ED2 | Freewheel level dec2 | 16#10CF = 4303 |  |  |  | Compatibility | R/WS | UINT (Unsigned16) | 1 % |  | 0 % ... 100 %
O_IL2 | Motor 2 current limit | 16#10D0 = 4304 |  |  |  | Compatibility | R/WS | UINT (Unsigned16) | 1 % |  | 150 % ... 700 %
O_AC2 | Motor 2 Acceleration time | 16#10D1 = 4305 |  |  |  | Compatibility | R/WS | UINT (Unsigned16) | 1 s |  | 1 s ... 60 s
O_DE2 | Motor 2 deceleration time | 16#10D2 = 4306 |  |  |  | Compatibility | R/WS | UINT (Unsigned16) | 1 s |  | 1 s ... 60 s
O_TI2 | Motor 2 decel loop gain | 16#10D3 = 4307 |  |  |  | Compatibility | R/WS | UINT (Unsigned16) | 1 % |  | 10 % ... 50 %
O_FCS | Factory / recall customer parameter set | 16#1130 = 4400 |  |  | O_FCS | Compatibility | R/WS | WORD (Enumeration) | -
O_RPR | Reset counter | 16#1131 = 4401 |  |  | O_RPR | Compatibility | R/W | WORD (Enumeration) | -
O_RTH | Reset motor thermal state | 16#1132 = 4402 |  |  | N_Y | Compatibility | R/WS | WORD (Enumeration) | -
O_VSP | Product software version | 16#1195 = 4501 |  |  |  | Compatibility | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
O_TSP | Product software type | 16#1196 = 4502 |  |  |  | Compatibility | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
O_ICL | Rating | 16#1197 = 4503 |  |  |  | Compatibility | R | UINT (Unsigned16) | 0.1 A |  | 0.0 A ... 1200.0 A
O_VCAL | Product range | 16#1198 = 4504 |  |  | O_VCAL | Compatibility | R | WORD (Enumeration) | -
O_NCD | Rating number | 16#1199 = 4505 |  |  | O_NCD | Compatibility | R | WORD (Enumeration) | -
O_STA | Product status | 16#FA01 = 64001 |  |  | O_STA | Compatibility | R | WORD (Enumeration) | -
O_KEY | Key saved | 16#FA08 = 64008 |  |  |  | Compatibility | R/WS | UINT (Unsigned16) | 1 |  | 0 ... 65535
AI1A | AI1 assignment | 16#12D5 = 4821 | 16#2012/16 | 16#79/01/16 = 121/01/22 | CSA | I/O parameters | R | WORD (Enumeration) | - |  |  | [AI1 assignment] (AI1A) | [AI1 assignment] (AI1A) [AI1] (AI1C)
EPF2 | EPF2 (external error detected by fieldbus) info | 16#1BE8 = 7144 | 16#2029/2D | 16#84/01/91 = 132/01/145 |  | Fault parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
TIMO | Local time offset | 16#1CE7 = 7399 | 16#202B/64 | 16#85/01/C8 = 133/01/200 |  | Configuration and settings | R/W | INT (Signed16) | 1 |  | -3072 ... 3584
CMD1 | Modbus command register | 16#213F = 8511 | 16#2037/C | 16#8B/01/70 = 139/01/112 |  | Control parameters | R | WORD (BitString16) | - |  |  | [Modbus Cmd] (CMD1) | [Command word image] (CWI)
CMD2 | CANopen command register | 16#2140 = 8512 | 16#2037/D | 16#8B/01/71 = 139/01/113 |  | Control parameters | R | WORD (BitString16) | - |  |  | [CANopen Cmd] (CMD2) | [Command word image] (CWI)
CMD3 | DrivecomCmdRegCom. | 16#2141 = 8513 | 16#2037/E | 16#8B/01/72 = 139/01/114 |  | Control parameters | R | WORD (BitString16) | - |  |  | [COM. Module cmd.] (CMD3) | [Command word image] (CWI)
NRP1 | Number of Received PDO1 words | 16#32F5 = 13045 | 16#2064/2E | 16#A2/01/2E = 162/01/46 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
NTP1 | Number of Transmit PDO1 words | 16#32FF = 13055 | 16#2064/38 | 16#A2/01/38 = 162/01/56 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
NRP2 | Number of Received PDO2 words | 16#32E1 = 13025 | 16#2064/1A | 16#A2/01/1A = 162/01/26 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
NTP2 | Number of Transmit PDO2 words | 16#32EB = 13035 | 16#2064/24 | 16#A2/01/24 = 162/01/36 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
NRP3 | Number of Received PDO3 words | 16#32CD = 13005 | 16#2064/6 | 16#A2/01/06 = 162/01/06 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
NTP3 | Number of Transmit PDO3 words | 16#32D7 = 13015 | 16#2064/10 | 16#A2/01/10 = 162/01/16 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
TWOC | Ethernet option - Word order | 16#FBD8 = 64472 |  |  | TWO | Communication parameters | R/WS | WORD (Enumeration) | - | [Modbus Word Order ON] HIGH
TP24 | Transmit PDO2-4 | 16#32EA = 13034 | 16#2064/23 | 16#A2/01/23 = 162/01/35 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Transmit PDO2-4] (TP24) | [PDO2 image] (P02)
TP23 | Transmit PDO2-3 | 16#32E9 = 13033 | 16#2064/22 | 16#A2/01/22 = 162/01/34 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Transmit PDO2-3] (TP23) | [PDO2 image] (P02)
TP21 | Transmit PDO2-1 | 16#32E7 = 13031 | 16#2064/20 | 16#A2/01/20 = 162/01/32 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Transmit PDO2-1] (TP21) | [PDO2 image] (P02)
S_TJD | Thyristor junction temperature | 16#35B8 = 13752 | 16#206B/35 | 16#A5/01/99 = 165/01/153 |  | Status parameters | R | INT (Signed16) | 1 °C |  | -100 °C ... 300 °C | [SCR Junction Temp] (S_TJD) | [Thermal Monitoring] (TPM)
RP24 | Receive PDO2-4 | 16#32E0 = 13024 | 16#2064/19 | 16#A2/01/19 = 162/01/25 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Receive PDO2-4] (RP24) | [PDO2 image] (P02)
FPTT | Fan total operation time | 16#0FF8 = 4088 | 16#200A/59 | 16#75/01/59 = 117/01/89 |  | Status parameters | R | UINT (Unsigned32) | 1 h |  | 0 h ... 4294967295 h | [Fan Total Op Time] (FPTT) | [Counter Management] (ELT)
TP22 | Transmit PDO2-2 | 16#32E8 = 13032 | 16#2064/21 | 16#A2/01/21 = 162/01/33 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Transmit PDO2-2] (TP22) | [PDO2 image] (P02)
REC1 | RX error counter | 16#17AB = 6059 | 16#201E/3C | 16#7F/01/3C = 127/01/60 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [RX Error Counter] (REC1) | [CANopen map] (CNM)
LSC | Stator loss compensation | 16#2685 = 9861 | 16#2044/3E | 16#92/01/3E = 146/01/62 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | Refer to programming manual | 0 % ... 90 % | [Stator Loss Comp] (LSC) | [Start & Stop] (SSP)
IM10 | Ethernet option IP mode | 16#FBC2 = 64450 |  |  | IPM | Configuration and settings | R/W | WORD (Enumeration) | - | [DHCP] DHCP |  | [ETH Option IP Mode] (IM10) | [Eth Module Config] (ETO)
CSCA | Cascade DI assignment | 16#10E0 = 4320 | 16#200D/15 | 16#76/01/79 = 118/01/121 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Cascade DI Assign] (CSCA) | [Cascade] (CSC)
NBTP | Number of TX PDO | 16#330E = 13070 | 16#2064/47 | 16#A2/01/47 = 162/01/71 |  | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Number of TX PDO] (NBTP) | [CANopen map] (CNM)
RP12 | Receive PDO1-2 | 16#32F2 = 13042 | 16#2064/2B | 16#A2/01/2B = 162/01/43 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Receive PDO1-2] (RP12) | [PDO1 image] (P01)
L3A | DI3 assignment | 16#12C3 = 4803 | 16#2012/4 | 16#79/01/04 = 121/01/04 | CSL | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [DI3 assignment] (L3A) | [Input/Output] (IO)
EBA | DC continuous braking time | 16#10EB = 4331 | 16#200D/20 | 16#76/01/84 = 118/01/132 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 20 % | 20 % ... 100 % | [DC Braking Time] (EBA) | [Simply start] (SIM) [Start & Stop] (SSP)
ODLA | Overload activation | 16#3854 = 14420 | 16#2072/15 | 16#A9/01/15 = 169/01/21 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Overload Activation] (ODLA) | [Process overload] (OLD)
L4A | DI4 assignment | 16#12C4 = 4804 | 16#2012/5 | 16#79/01/05 = 121/01/05 | CSL | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [DI4 assignment] (L4A) | [Input/Output] (IO)
TIM2 | Motor 2 torque control deceleration gain | 16#261D = 9757 | 16#2043/3A | 16#91/01/9E = 145/01/158 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 40 % | 10 % ... 50 % | [Dec Gain Motor 2] (TIM2) | [2nd Mot Parameters] (ST2)
S_BRC | Dynamic braking level | 16#10EA = 4330 | 16#200D/1F | 16#76/01/83 = 118/01/131 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 50 % | 0 % ... 100 % | [Braking Level] (S_BRC) | [Simply start] (SIM) [Start & Stop] (SSP)
EDC | End of controled deceleration threshold | 16#2693 = 9875 | 16#2044/4C | 16#92/01/4C = 146/01/76 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 20 % | 0 % ... 100 % | [End Of Deceleration] (EDC) | [Simply start] (SIM) [Start & Stop] (SSP)
M2CT | Mdb NET frames | 16#178F = 6031 | 16#201E/20 | 16#7F/01/20 = 127/01/32 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Mdb NET frames] (M2CT) | [Modbus HMI Diag] (MDH)
DO2S | DQ2 active at | 16#10A6 = 4262 | 16#200C/3F | 16#76/01/3F = 118/01/63 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [High level] POS |  | [DQ2 Active at] (DO2S) | [DQ2 Configuration] (DO2)
DCR | End of start current threshold | 16#71AD = 29101 | 16#2105/2 | 16#F2/01/66 = 242/01/102 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 25 % | 0 % ... 100 % | [End of Start Cur Thd] (DCR) | [Start & Stop] (SSP)
RSFT | Thermal error reset assignment | 16#1BF8 = 7160 | 16#2029/3D | 16#84/01/A1 = 132/01/161 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Th Error Reset Assign] (RSFT) | [Fault reset] (RST)
TP34 | Transmit PDO3-4 | 16#32D6 = 13014 | 16#2064/F | 16#A2/01/0F = 162/01/15 |  | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Transmit PDO3-4] (TP34) | [PDO3 image] (P03)
V0 | Initial starting voltage | 16#268C = 9868 | 16#2044/45 | 16#92/01/45 = 146/01/69 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 49 % | 25 % ... 49 % | [Init Starting Voltage] (V0) | [Start & Stop] (SSP)
NMTS | Canopen NMT state | 16#17A9 = 6057 | 16#201E/3A | 16#7F/01/3A = 127/01/58 | NMTS | Status parameters | R | WORD (Enumeration) | - |  |  | [Canopen NMT state] (NMTS) | [CANopen map] (CNM)
RP11 | Receive PDO1-1 | 16#32F1 = 13041 | 16#2064/2A | 16#A2/01/2A = 162/01/42 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Receive PDO1-1] (RP11) | [PDO1 image] (P01)
RP13 | Receive PDO1-3 | 16#32F3 = 13043 | 16#2064/2C | 16#A2/01/2C = 162/01/44 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Receive PDO1-3] (RP13) | [PDO1 image] (P01)
TP31 | Transmit PDO3-1 | 16#32D3 = 13011 | 16#2064/C | 16#A2/01/0C = 162/01/12 |  | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Transmit PDO3-1] (TP31) | [PDO3 image] (P03)
ACM2 | Motor 2 acceleration time | 16#261B = 9755 | 16#2043/38 | 16#91/01/9C = 145/01/156 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 15 s | 1 s ... 60 s | [Acceleration Motor 2] (ACM2) | [2nd Mot Parameters] (ST2)
M1CT | Mdb frame number | 16#177B = 6011 | 16#201E/C | 16#7F/01/0C = 127/01/12 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Mdb Frame Nb] (M1CT) | [Modbus network diag] (MND)
RP33 | Receive PDO3-3 | 16#32CB = 13003 | 16#2064/4 | 16#A2/01/04 = 162/01/04 |  | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Receive PDO3-3] (RP33) | [PDO3 image] (P03)
TQM2 | Motor 2 initial starting torque | 16#2618 = 9752 | 16#2043/35 | 16#91/01/99 = 145/01/153 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 20 % | 0 % ... 100 % | [Init Start Torque Mot 2] (TQM2) | [2nd Mot Parameters] (ST2)
S_IPR | Preheating level | 16#10D7 = 4311 | 16#200D/C | 16#76/01/70 = 118/01/112 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [Preheat Level] (S_IPR) | [Preheating] (PRF)
CSC | Cascade function activation | 16#10E1 = 4321 | 16#200D/16 | 16#76/01/7A = 118/01/122 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Cascade Activation] (CSC) | [Cascade] (CSC)
DLT | Inside Delta wiring | 16#10F4 = 4340 | 16#200D/29 | 16#76/01/8D = 118/01/141 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Inside Delta] (DLT) | [Motor wiring] (MWMT)
SST | Small motor test | 16#10FE = 4350 | 16#200D/33 | 16#76/01/97 = 118/01/151 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Small Motor Test] (SST) | [Motor wiring] (MWMT)
TIMF | Time format | 16#1CE2 = 7394 | 16#202B/5F | 16#85/01/C3 = 133/01/195 | TIMF | Configuration and settings | R/W | WORD (Enumeration) | - | [24h] 24 |  | [Time Format] (TIMF) | [Date & Time] (DTO)
IN | Nominal current | 16#2684 = 9860 | 16#2044/3D | 16#92/01/3D = 146/01/61 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 A | Refer to programming manual | 0.1 A ... 6553.5 A | [Motor Nom Current] (IN) | [Simply start] (SIM) [Motor parameters] (MPA)
ETXO | Ethernet option Tx frames | 16#FBD4 = 64468 |  |  |  | Configuration and settings | R | UINT (Unsigned32) | 1 |  | 0 ... 4294967295 | [ETH opt Tx frames] (ETXO) | [Ethernet Module Diag] (MTE)
S_BST | Voltage boost level | 16#2686 = 9862 | 16#2044/3F | 16#92/01/3F = 146/01/63 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [Boost] (S_BST) | [Start & Stop] (SSP)
ERXO | Ethernet option Rx frames | 16#FBD2 = 64466 |  |  |  | Configuration and settings | R | UINT (Unsigned32) | 1 |  | 0 ... 4294967295 | [ETH opt Rx frames] (ERXO) | [Ethernet Module Diag] (MTE)
CLB | Response to control supply loss | 16#1B71 = 7025 | 16#2028/1A | 16#84/01/1A = 132/01/26 | CLB | Configuration and settings | R/WS | WORD (Enumeration) | - | [Error triggered] 0 |  | [Control Supply Loss] (CLB) | [Error/Warning handling] (CSWM)
TSC | Gamma synchro error | 16#71AC = 29100 | 16#2105/1 | 16#F2/01/65 = 242/01/101 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 8 | 0 ... 11 | [Gamma Sync Error] (TSC) | [Monitoring] (PROT)
TLI | Torque limit | 16#2690 = 9872 | 16#2044/49 | 16#92/01/49 = 146/01/73 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 9 % | 9 % ... 200 % | [Torque Limit] (TLI) | [Start & Stop] (SSP)
CLP | Control mode | 16#268E = 9870 | 16#2044/47 | 16#92/01/47 = 146/01/71 | CLP | Configuration and settings | R/WS | WORD (Enumeration) | - | [Torque control (TCS)] TC |  | [Control Mode] (CLP) | [Start & Stop] (SSP)
S_LTR | Motor torque | 16#2692 = 9874 | 16#2044/4B | 16#92/01/4B = 146/01/75 |  | Status parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % | [Motor Torque] (S_LTR) | [Motor parameters] (MMO)
INM2 | Motor 2 nominal current | 16#2616 = 9750 | 16#2043/33 | 16#91/01/97 = 145/01/151 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 A | Refer to programming manual | 0.1 A ... 6553.5 A | [Nom Current Motor 2] (INM2) | [2nd Mot Parameters] (ST2)
TLM2 | Motor 2 torque limit | 16#2617 = 9751 | 16#2043/34 | 16#91/01/98 = 145/01/152 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 9 % | 9 % ... 200 % | [Torque Limit Motor 2] (TLM2) | [2nd Mot Parameters] (ST2)
M1EC | Mdb NET CRC errors | 16#177A = 6010 | 16#201E/B | 16#7F/01/0B = 127/01/11 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Mb NET CRC errors] (M1EC) | [Modbus network diag] (MND)
RP22 | Receive PDO2-2 | 16#32DE = 13022 | 16#2064/17 | 16#A2/01/17 = 162/01/23 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Receive PDO2-2] (RP22) | [PDO2 image] (P02)
RP23 | Receive PDO2-3 | 16#32DF = 13023 | 16#2064/18 | 16#A2/01/18 = 162/01/24 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Receive PDO2-3] (RP23) | [PDO2 image] (P02)
TP11 | Transmit PDO1-1 | 16#32FB = 13051 | 16#2064/34 | 16#A2/01/34 = 162/01/52 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Transmit PDO1-1] (TP11) | [PDO1 image] (P01)
NBRP | Number of RX PDO | 16#330F = 13071 | 16#2064/48 | 16#A2/01/48 = 162/01/72 |  | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Number of RX PDO] (NBRP) | [CANopen map] (CNM)
FFSA | Freewheel stop assignment | 16#2BC7 = 11207 | 16#2052/8 | 16#99/01/08 = 153/01/08 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Digital input 3] LI3 |  | [Freewheel Assign] (FFSA) | [Start & Stop] (SSP)
CMDC | Command channel | 16#FA28 = 64040 |  |  | CNL | Status parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (CMDC) | [Communication map] (CMM)
BPTN | Total bypass cycle count | 16#103A = 4154 | 16#200B/37 | 16#75/01/9B = 117/01/155 |  | Configuration and settings | R | UINT (Unsigned32) | 1 |  | 0 ... 4294967295 | [Total Bypass Cycles] (BPTN) | [Counter Management] (ELT)
THRC | Copper motor thermal state | 16#268B = 9867 | 16#2044/44 | 16#92/01/44 = 146/01/68 |  | Status parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 300 % | [Copper Mot Th State] (THRC) | [Thermal Monitoring] (TPM)
RP21 | Receive PDO2-1 | 16#32DD = 13021 | 16#2064/16 | 16#A2/01/16 = 162/01/22 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Receive PDO2-1] (RP21) | [PDO2 image] (P02)
S_COS | Power factor | 16#2586 = 9606 | 16#2042/7 | 16#91/01/07 = 145/01/07 |  | Status parameters | R | UINT (Unsigned16) | 0.01 |  | 0.00 ... 1.00 | [Power Factor] (S_COS) | [Motor parameters] (MMO)
RP34 | Receive PDO3-4 | 16#32CC = 13004 | 16#2064/5 | 16#A2/01/05 = 162/01/05 |  | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Receive PDO3-4] (RP34) | [PDO3 image] (P03)
RP31 | Receive PDO3-1 | 16#32C9 = 13001 | 16#2064/2 | 16#A2/01/02 = 162/01/02 |  | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Receive PDO3-1] (RP31) | [PDO3 image] (P03)
TQ0 | Initial starting torque | 16#268F = 9871 | 16#2044/48 | 16#92/01/48 = 146/01/72 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 20 % | 0 % ... 100 % | [Init Starting Torque] (TQ0) | [Simply start] (SIM) [Start & Stop] (SSP)
BPCN | Bypass cycle count | 16#103C = 4156 | 16#200B/39 | 16#75/01/9D = 117/01/157 |  | Configuration and settings | R/WS | UINT (Unsigned32) | 1 | 0 | 0 ... 4294967295 | [Bypass Cycle Count] (BPCN) | [Counter Management] (ELT)
LIS | Second motor selection assignment | 16#261E = 9758 | 16#2043/3B | 16#91/01/9F = 145/01/159 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [2nd Mot Assign] (LIS) | [2nd Mot Parameters] (ST2)
PTHH | Power-on time | 16#0CCC = 3276 | 16#2002/4D | 16#71/01/4D = 113/01/77 |  | Configuration and settings | R/WS | UINT (Unsigned32) | 0.1 h |  | 0.0 h ... 429496729.5 h | [Power-on time] (PTHH) | [Counter Management] (ELT)
TIG | Torque control deceleration gain | 16#2691 = 9873 | 16#2044/4A | 16#92/01/4A = 146/01/74 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 40 % | 10 % ... 50 % | [Deceleration Gain] (TIG) | [Start & Stop] (SSP)
EDM2 | Motor 2 end of controled deceleration threshold | 16#2619 = 9753 | 16#2043/36 | 16#91/01/9A = 145/01/154 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 20 % | 0 % ... 100 % | [End Of Dec Motor 2] (EDM2) | [2nd Mot Parameters] (ST2)
LAC | Access level | 16#0BBE = 3006 | 16#2000/7 | 16#70/01/07 = 112/01/07 | LAC | Configuration and settings | R/W | WORD (Enumeration) | - | [Standard access] STD |  | [Access Level] (LAC) | [Parameter access] (PAC)
TP33 | Transmit PDO3-3 | 16#32D5 = 13013 | 16#2064/E | 16#A2/01/0E = 162/01/14 |  | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Transmit PDO3-3] (TP33) | [PDO3 image] (P03)
M2EC | Mdb NET CRC errors | 16#178E = 6030 | 16#201E/1F | 16#7F/01/1F = 127/01/31 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Mdb NET CRC errors] (M2EC) | [Modbus HMI Diag] (MDH)
S_LUL | Underload threshold | 16#384F = 14415 | 16#2072/10 | 16#A9/01/10 = 169/01/16 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 60 % | 0 % ... 100 % | [Underload Threshold] (S_LUL) | [Process underload] (ULD)
COM1 | Modbus com. status | 16#FA2F = 64047 |  |  | COM1 | Status parameters | R | WORD (Enumeration) | - |  |  | [Mdb com stat] (COM1) | [Modbus network diag] (MND)
DLTS | Inside Delta diagnostics status | 16#10F6 = 4342 | 16#200D/2B | 16#76/01/8F = 118/01/143 | DLTS | Status parameters | R | WORD (Enumeration) | - |  |  | [In Delta Diag Status] (DLTS) | [Motor wiring] (MWMT) [Motor parameters] (MMO)
DLTL | Inside Delta diagnostics | 16#10F5 = 4341 | 16#200D/2A | 16#76/01/8E = 118/01/142 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [In Delta Diag] (DLTL) | [Motor wiring] (MWMT)
S_ACC | Acceleration ramp time | 16#2364 = 9060 | 16#203C/3D | 16#8E/01/3D = 142/01/61 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 15 s | 1 s ... 60 s | [Acceleration] (S_ACC) | [Simply start] (SIM) [Start & Stop] (SSP)
TPR | Time before preheat | 16#10D8 = 4312 | 16#200D/D | 16#76/01/71 = 118/01/113 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 min | 5 min | 0 min ... 999 min | [Time Before Preheat] (TPR) | [Preheating] (PRF)
RP14 | Receive PDO1-4 | 16#32F4 = 13044 | 16#2064/2D | 16#A2/01/2D = 162/01/45 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Receive PDO1-4] (RP14) | [PDO1 image] (P01)
RP32 | Receive PDO3-2 | 16#32CA = 13002 | 16#2064/3 | 16#A2/01/03 = 162/01/03 |  | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Receive PDO3-2] (RP32) | [PDO3 image] (P03)
EBAL | Battery level | 16#1CE4 = 7396 | 16#202B/61 | 16#85/01/C5 = 133/01/197 |  | Status parameters | R | INT (Signed16) | 1 % |  | -1 % ... 100 % | [Battery Level] (EBAL) | [Date & Time] (DTO)
S_DEC | Deceleration ramp time | 16#2365 = 9061 | 16#203C/3E | 16#8E/01/3E = 142/01/62 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 15 s | 1 s ... 60 s | [Deceleration] (S_DEC) | [Simply start] (SIM) [Start & Stop] (SSP)
DEM2 | Motor 2 deceleration time | 16#261C = 9756 | 16#2043/39 | 16#91/01/9D = 145/01/157 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 15 s | 1 s ... 60 s | [Deceleration Motor 2] (DEM2) | [2nd Mot Parameters] (ST2)
COM2 | Mdb com stat | 16#FA30 = 64048 |  |  | COM1 | Status parameters | R | WORD (Enumeration) | - |  |  | [Mdb com stat] (COM2) | [Modbus HMI Diag] (MDH)
S_TLS | Excessive starting time | 16#2688 = 9864 | 16#2044/41 | 16#92/01/41 = 146/01/65 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 9 s | 0 s ... 999 s | [Too Long Start] (S_TLS) | [Monitoring] (PROT)
TP13 | Transmit PDO1-3 | 16#32FD = 13053 | 16#2064/36 | 16#A2/01/36 = 162/01/54 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Transmit PDO1-3] (TP13) | [PDO1 image] (P01)
TP12 | Transmit PDO1-2 | 16#32FC = 13052 | 16#2064/35 | 16#A2/01/35 = 162/01/53 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Transmit PDO1-2] (TP12) | [PDO1 image] (P01)
TP14 | Transmit PDO1-4 | 16#32FE = 13054 | 16#2064/37 | 16#A2/01/37 = 162/01/55 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Transmit PDO1-4] (TP14) | [PDO1 image] (P01)
S_TBS | Time before motor restart | 16#2687 = 9863 | 16#2044/40 | 16#92/01/40 = 146/01/64 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 2 s | 0 s ... 999 s | [Time Before Restart] (S_TBS) | [Monitoring] (PROT)
ILM2 | Motor 2 current limit | 16#261A = 9754 | 16#2043/37 | 16#91/01/9B = 145/01/155 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 400 % | 150 % ... 700 % | [Current Limit Motor 2] (ILM2) | [2nd Mot Parameters] (ST2)
PRHA | Preheating assignment | 16#10D6 = 4310 | 16#200D/B | 16#76/01/6F = 118/01/111 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Preheating Assign] (PRHA) | [Preheating] (PRF)
AO1S | Analog output AQ1 scaling | 16#1249 = 4681 | 16#2010/52 | 16#78/01/52 = 120/01/82 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 200 % | 50 % ... 500 % | [AQ1 Scaling] (AO1S) | [AQ1 configuration] (AO1)
S_PHR | Phase Inversion Monitoring | 16#0C4E = 3150 | 16#2001/33 | 16#70/01/97 = 112/01/151 | S_PHR | Configuration and settings | R/WS | WORD (Enumeration) | - | [No monitoring] NO |  | [Phase Inversion Mon] (S_PHR) | [Monitoring] (PROT)
THSD | Device temperature | 16#0FFA = 4090 | 16#200A/5B | 16#75/01/5B = 117/01/91 |  | Status parameters | R | INT (Signed16) | 1 °C |  | -100 °C ... 200 °C | [Device Temperature] (THSD) | [Thermal Monitoring] (TPM)
EERO | Ethernet option error frames | 16#FBD6 = 64470 |  |  |  | Configuration and settings | R | UINT (Unsigned32) | 1 |  | 0 ... 4294967295 | [ETH opt error frames] (EERO) | [Ethernet Module Diag] (MTE)
TES | Minimum start time | 16#71AE = 29102 | 16#2105/3 | 16#F2/01/67 = 242/01/103 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 500 ms | 0 ms ... 10000 ms | [Minimum Start Time] (TES) | [Start & Stop] (SSP)
TP32 | Transmit PDO3-2 | 16#32D4 = 13012 | 16#2064/D | 16#A2/01/0D = 162/01/13 |  | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Transmit PDO3-2] (TP32) | [PDO3 image] (P03)
TEC1 | TX error counter | 16#17AA = 6058 | 16#201E/3B | 16#7F/01/3B = 127/01/59 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [TX Error Counter] (TEC1) | [CANopen map] (CNM)
UDLA | Underload activation | 16#384A = 14410 | 16#2072/B | 16#A9/01/0B = 169/01/11 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Underload Activation] (UDLA) | [Process underload] (ULD)
LET | External error condition | 16#1BB2 = 7090 | 16#2028/5B | 16#84/01/5B = 132/01/91 | L_H | Configuration and settings | R/WS | WORD (Enumeration) | - | [Active high] HIG |  | [Ext Error Condition] (LET) | [External error] (ETF)
S_ULN | Mains voltage | 16#0C51 = 3153 | 16#2001/36 | 16#70/01/9A = 112/01/154 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | 400 V | 170 V ... 750 V | [Mains Voltage] (S_ULN) | [Simply start] (SIM) [Motor parameters] (MPA)
DATF | Date format | 16#1CE3 = 7395 | 16#202B/60 | 16#85/01/C4 = 133/01/196 | DATF | Configuration and settings | R/W | WORD (Enumeration) | - | [yyyy/mm/dd] Y4M2D2 |  | [Date Format] (DATF) | [Date & Time] (DTO)
RFLT | Clear error history | 16#0C31 = 3121 | 16#2001/16 | 16#70/01/7A = 112/01/122 | N_Y | Configuration and settings | R | WORD (Enumeration) | - | [No] NO |  | [Clear Error History] (RFLT) | [Diag. data] (DDT)
RTHH | Motor run time | 16#0CCA = 3274 | 16#2002/4B | 16#71/01/4B = 113/01/75 |  | Configuration and settings | R/WS | UINT (Unsigned32) | 0.1 h |  | 0.0 h ... 429496729.5 h | [Motor Run Time] (RTHH) | [Counter Management] (ELT)
RTHR | Reset motor thermal state | 16#268A = 9866 | 16#2044/43 | 16#92/01/43 = 146/01/67 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Mot Th State Reset] (RTHR) | [Monitoring] (PROT)
TOUT | Ethernet timeout | 16#FAD3 = 64211 |  |  |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 10.0 s | 0.1 s ... 60.0 s | [Ethernet Timeout] (TOUT) | [Eth Module Config] (ETO)

## Enumerations
List ID | Value | Display | Description
AIOT | 1 | [Voltage] (10U) | Voltage
| 2 | [Current] (0A) | Current
| 7 | [PTC] (PTC) | PTC
| 10 | [PT100] (1PT2) | PT100
| 15 | [PT100 in 3 wires] (1PT23) | PT100 in 3 wires
ALR | 0 | [No Warning stored] (NOA) | No warning stored
| 35 | [Device Therm Warn] (THA) | Device thermal state warning
| 40 | [Ext. Error Warning] (EFA) | External error warning
| 41 | [Undervoltage Warning] (USA) | Undervoltage warning
| 56 | [Process Undld Warning] (ULA) | Process underload warning
| 57 | [Process Overload Warning] (OLA) | Process overload warning
| 60 | [Dev Thermal reached] (TAD) | Device thermal threshold reached
| 87 | [AI1 Th Warning] (TP1A) | AI1 thermal sensor warning
| 90 | [Motor Overload Warn] (OLMA) | Motor overload warning
| 91 | [Low Battery Warn] (RBLA) | Low Battery warning
| 92 | [No Battery Warn] (RBNA) | Battery not detected warning
| 93 | [Invalid RTC Warn] (RTCA) | Invalid RTC warning
| 94 | [Bypass Warn] (BPA) | Bypass warning
| 95 | [Modbus Com Warn] (SLLA) | Modbus comm interruption warning
| 96 | [Fieldbus Com Warn] (CLLA) | Fieldbus comm interruption warning
| 111 | [CANopen Com Warn] (COLA) | CANOpen comm interruption warning
| 132 | [Inhibited Errors Warn] (INH) | Inhibited errors warning
| 133 | [Temp Sens AI1 Warn] (TS1A) | Temperature sensor AI1 warning
BDCO | 38 | [50 kbps] (50K) | Baud rate 50kbps
| 52 | [125 kbps] (125K) | Baud rate 125kbps
| 60 | [250 kbps] (250K) | Baud rate 250kbps
| 68 | [500 kbps] (500K) | Baud rate 500kbps
| 76 | [1 Mbps] (1M) | Baud rate 1Mbps
BMP | 0 | [Stop On Switching] (STOP) | Stop on switching
| 1 | [Bumpless] (BUMP) | Bumpless
| 2 | [Disabled] (DIS) | Disabled
CDX | 1 | [Terminals] (TER) | Terminal block
| 3 | [HMI] (LCC) | Local HMI
| 10 | [Modbus] (MDB) | Modbus communication
| 20 | [CANopen] (CAN) | CANopen communication
| 30 | [Com. Module] (NET) | Ext. communication module
CHCF | 0 | [Standard Profile] (STD) | Standard profile
| 4 | [SE8 Profile] (SE8) | SE8 profile
CINR | 20 | [0.001] (0001) | 0.001
| 30 | [0.01] (001) | 0.01
| 40 | [0.1] (01) | 0.1
| 50 | [1] (1) | 1
| 60 | [10] (10) | 10
CLB | 0 | [Error] (0) | Error triggered
| 1 | [Error w/o Relay] (1) | Error triggered w/o relay
| 2 | [Warning] (2) | Warning triggered
CLP | 0 | [Voltage Control] (VC) | Voltage control
| 1 | [Torque Control] (TC) | Torque control (TCS)
| 2 | [Current Control] (CC) | Current control
CNFS | 0 | [In progress] (NO) | In progress
| 1 | [Config. No.0] (CNF0) | Configuration 0 active
CNL | 0 | [Terminals] (TER) | Terminal block
| 2 | [HMI] (LCC) | Local HMI
| 3 | [Modbus] (MDB) | Modbus communication 1
| 6 | [CANopen] (CAN) | CANopen communication
| 9 | [Com. Module] (NET) | Ext. communication module
| 11 | [Ethernet Module] (ETH) | Ethernet option module
| 15 | [PC tool] (PWS) | PC tool
| 16 | [Not Available] (NA) | Not available
COM1 | 0 | [R0T0] (R0T0) | R0T0
| 1 | [R0T1] (R0T1) | R0T1
| 2 | [R1T0] (R1T0) | R1T0
| 3 | [R1T1] (R1T1) | R1T1
COP | 0 | [No] (NO) | No copy
| 2 | [Command] (CD) | Copy command
CSA | 0 | [No] (NO) | Not assigned
| 1 | [AQ1] (AO1) | Analog output AQ1
| 163 | [Forced local] (AIFLOC) | Forced loc mode channel
| 350 | [AI1 Th Monitoring] (TH1S) | AI1 thermal monitoring
CSL | 0 | [No] (NO) | No
| 17 | [Forced Local] (LIFLO) | Forced local mode
| 18 | [Fault Reset] (LIRSF) | Fault Reset
| 27 | [External Error] (LIETF) | External error
| 40 | [Cmd switching] (LICCS) | Switch cmd channel
| 41 | [Disable Error Detect] (LIINH) | Disable error detection
| 61 | [Device Lock] (LILES) | Device lock
| 145 | [R1] (R1) | Relay R1
| 146 | [R2] (R2) | Relay R2
| 147 | [R3] (R3) | Relay R3
| 161 | [DQ1] (DO1) | Digital ouptut DQ1
| 228 | [DQ2] (DO2) | Digital ouptut DQ2
| 403 | [Freewheel Stop] (FFSA) | Freewheel stop
| 404 | [Th Error Reset] (RSFT) | Thermal error reset
| 405 | [Cascade] (CSCA) | Cascade
| 406 | [2nd Mot Param Set] (LIS) | Second motor parameter selection
| 407 | [Preheating] (PRHA) | Preheating
| 409 | [Stop] (STOP) | Stop
| 410 | [Run] (RUN) | Run
CSLOUT | 0 | [No] (NO) | No
| 146 | [R2] (R2) | Relay R2
| 147 | [R3] (R3) | Relay R3
| 161 | [DQ1] (DO1) | Digital ouptut DQ1
| 228 | [DQ2] (DO2) | Digital ouptut DQ2
DATF | 0 | [yyyy/mm/dd] (Y4M2D2) | yyyy/mm/dd
| 1 | [dd/mm/yyyy] (D2M2Y4) | dd/mm/yyyy
| 2 | [mm/dd/yyyy] (M2D2Y4) | mm/dd/yyyy
| 3 | [dd/mm/yy] (D2M2Y2) | dd/mm/yy
| 4 | [dd/mm] (D2M2) | dd/mm
DLTS | 0 | [Not Done] (NA) | Not done
| 1 | [Passed] (OK) | Passed
| 2 | [Invert L2 & L3] (32) | Invert L2 and L3
| 3 | [Invert L1 & L2] (21) | Invert L1 and L2
| 4 | [Invert L1 & L3] (31) | Invert L1 and L3
| 5 | [Change 123 to 312] (312) | Change 123 to 312
| 6 | [Change 123 to 231] (231) | Change 123 to 231
| 7 | [Bad Motor Wiring] (MOT) | Bad motor cable wiring
| 8 | [Unknown Error] (UNK) | Unknown error
| 9 | [Pending] (PEND) | Pending
DPMA | 1 | [Master 1] (1) | Master 1
| 2 | [Master 2] (2) | Master 2
DUR | 0 | [5 minutes] (5) | 5 minutes
| 1 | [10 minutes] (10) | 10 minutes
| 2 | [30 minutes] (30) | 30 minutes
| 3 | [1 hour] (1H) | 1 hour
| 4 | [2 hours] (2H) | 2 hours
| 5 | [3 hours] (3H) | 3 hours
| 6 | [Unlimited] (CT) | Unlimited
ECFG | 0 | [Ignore] (NO) | Ignore
| 1 | [Freewheel Stop] (YES) | Freewheel stop
| 2 | [Per STT] (STT) | Per STT
| 9 | [Deceleration] (DEC) | Controlled deceleration
| 10 | [Braking] (BRK) | Dynamic braking
EFDR | 0 | [No Error] (NO) | No error
| 1 | [Server Timeout] (TOUT) | Server timeout
| 2 | [Server No File] (SNF) | Server no file
| 3 | [Server Corrupt File] (CRPT) | Server corrupt file
| 4 | [Server Empty File] (EPTY) | Server empty file
| 5 | [Device Invalid File] (HINV) | Device invalid file
| 6 | [CRC Error] (CRC) | CRC error
| 7 | [Version Incompatibility] (VRM) | Version incompatibility
| 9 | [Device No File] (HNF) | Device no file
| 10 | [Server Reading Size] (SIZE) | Server reading Size
| 11 | [Device Opening File] (OPEN) | Device opening file
| 12 | [Device Reading File] (READ) | Device reading file
| 13 | [Incompatibility] (SCNT) | Incompatibility
| 14 | [Device Invalid Name] (NINV) | Device invalid name
| 15 | [Server Incorrect File Size] (FSIZ) | Server incorrect file size
| 16 | [Device Writing File] (HWF) | Device writing file
| 17 | [Server Writing File] (SWF) | Server writing file
ERRD | 16#0000 | [No Error] (NOF) | No error detected
| 16#0000 | [Inhibited Errors] (INH) | Inhibited errors
| 16#1000 | [Internal Error 14] (INFE) | Internal error 14 (CPU)
| 16#1000 | [Channel Switch Error] (CSF) | Channel switching detected error
| 16#2310 | [Overcurrent] (OCF) | Overcurrent
| 16#2311 | [Process Overload] (OLC) | Process overload
| 16#2330 | [Ground Short Circuit] (SCF3) | Ground short circuit
| 16#2350 | [Motor Overload] (OLF) | Motor overload
| 16#3110 | [Phase Loss] (PHF3) | Phase loss error
| 16#3120 | [Supply Mains UnderV] (USF) | Supply mains undervoltage
| 16#3130 | [Phase Inversion] (PIF) | Phase inversion
| 16#3130 | [Mains Direction Error] (PHF2) | Mains direction error
| 16#3130 | [Mains Loss] (PHF4) | Mains loss error
| 16#3130 | [Mains Sync Error] (PHF1) | Mains synchronization error
| 16#3130 | [In Delta Wiring Error] (DWF) | Inside Delta wiring error
| 16#3140 | [Mains Freq Error] (FRF) | Mains frequency out of tolerance
| 16#4210 | [Device Overheating] (OHF) | Device overheating
| 16#4210 | [AI1 Th Level Error] (TH1F) | AI1 thermal level error
| 16#5000 | [Input Contactor] (LCF) | input contactor
| 16#5100 | [Control Supply Error] (CLF) | Control supply error
| 16#5100 | [Internal Error 8] (INF8) | Internal error 8 (Switching Supply)
| 16#5100 | [Internal Error 10] (INFA) | Internal error 10 (Mains)
| 16#5100 | [Bypass Error] (BYF) | Bypass error
| 16#5100 | [Cust Supply Error] (CPSF) | Customer supply error
| 16#5500 | [Internal Error 15] (INFF) | Internal error 15 (Flash)
| 16#5530 | [Control Memory Error] (EEF1) | Control memory error
| 16#5530 | [Power Memory Error] (EEF2) | Power memory error
| 16#6100 | [Internal Link Error] (ILF) | Internal communication interruption with option module
| 16#6100 | [Internal Error 1] (INF1) | Internal error 1 (Rating)
| 16#6100 | [Internal Error 3] (INF3) | Internal error 3 (Intern Comm)
| 16#6100 | [Internal Error 4] (INF4) | Internal error 4 (Manufacturing)
| 16#6100 | [Internal Error 6] (INF6) | Internal error 6 (Option)
| 16#6100 | [Boards Compatibility] (HCF) | Boards compatibility
| 16#6100 | [Internal Error 21] (INFL) | Internal error 21 (RTC)
| 16#6100 | [Internal Error 25] (INFP) | Internal error 25 (Incompatibility CB & SW)
| 16#6100 | [Internal Error 35] (INFZ) | Internal error 35 (Invalid firmware version)
| 16#6300 | [Incorrect Config] (CFF) | Incorrect configuration
| 16#6300 | [Invalid Configuration] (CFI) | Invalid configuration
| 16#6300 | [Conf Transfer Error] (CFI2) | Configuration transfer error
| 16#6300 | [Security Files Corrupt] (SPFC) | Security files corrupt
| 16#6300 | [Sec Policy Update Err] (SPTF) | Security policy update error
| 16#6300 | [Config Change] (CFF2) | Configuration change
| 16#7000 | [Firmware Update Error] (FWER) | Firmware Update error
| 16#7000 | [Firmware Pairing Error] (FWPF) | Firmware pairing error
| 16#7000 | [No Power Comm Error] (FWMC) | No power communication error
| 16#7121 | [Lock Rotor Error] (LRF) | Lock rotor error
| 16#7121 | [Too Long Start Error] (TLSF) | Too long start error
| 16#7300 | [AI1 Thermal Sensor Error] (T1CF) | Thermal sensor error on AI1
| 16#7500 | [CANopen Init Error] (COLF) | CANopen initialization error
| 16#7510 | [Modbus Com Interruption] (SLF1) | Modbus communication interruption
| 16#7510 | [HMI Com Interruption] (SLF3) | HMI communication interruption
| 16#7520 | [Fieldbus Com Interrupt] (CNF) | Fieldbus communication interruption
| 16#7530 | [PC Com Interruption] (SLF2) | PC communication interruption
| 16#8100 | [CANopen Com Interrupt] (COF) | CANopen communication interruption
| 16#9000 | [External Error] (EPF1) | External detected error
| 16#9000 | [Fieldbus Error] (EPF2) | External error detected by Fieldbus
| 16#9000 | [FDR 2 Error] (FDR2) | FDR Eth module error
| 16#FF00 | [Simu Mains Detected] (SMPF) | Mains detected in simulation mode
| 16#FF03 | [Process Underload] (ULF) | Process underload
FCS | 0 | [No] (NO) | No
| 1 | [Recall customer parameter set 0] (REC0) | Recall customer parameter set 0
| 2 | [Recall customer parameter set 1] (REC1) | Recall customer parameter set 1
| 3 | [Recall customer parameter set 2] (REC2) | Recall customer parameter set 2
| 4 | [Recall customer parameter set 3] (REC3) | Recall customer parameter set 3
| 64 | [Recall default parameter set] (INI) | Recall default parameter set
FDRA | 0 | [NOT ACTIVE] (IDLE) | NOT ACTIVE
| 1 | [SAVE] (SAVE) | SAVE
| 2 | [REST] (REST) | REST
FOR | 2 | [8-O-1] (8O1) | 8bit odd parity 1stop bit
| 3 | [8-E-1] (8E1) | 8 bits even parity 1 stop bit
| 4 | [8-N-1] (8N1) | 8bit no parity 1stop bit
| 5 | [8-N-2] (8N2) | 8bit no parity 2stop bits
FRC | 0 | [Auto] (AUTO) | Auto detection of mains frequency
| 1 | [50Hz] (50) | 50 Hz
| 2 | [60Hz] (60) | 60 Hz
HMIS | 2 | [Ready] (RDY) | Ready
| 3 | [Freewheel] (NST) | Freewheel stop
| 4 | [Running] (RUN) | Running
| 5 | [Accelerating] (ACC) | Accelerating
| 6 | [Decelerating] (DEC) | Decelerating
| 7 | [Current Limitation] (CLI) | In current limitation
| 11 | [No Mains Voltage] (NLP) | No mains voltage
| 18 | [TC Mode Active] (TC) | TC mode active
| 19 | [In autotest] (ST) | In autotest
| 20 | [Autotest error] (FA) | Autotest error
| 21 | [Autotest OK] (OK) | Autotest OK
| 22 | [EEprom test] (EP) | EEprom test
| 23 | [Operating State "Fault"] (FLT) | Operating state "Fault"
| 25 | [DCP Flashing Mode] (DCP) | DCP Flashing mode
| 30 | [STO active] (STO) | STO active
| 36 | [Firmware Update] (FWUP) | Firmware Update
| 63 | [Motor Preheating] (HEA) | Motor preheating in progress
| 64 | [Bypassed] (BYP) | Bypassed
| 65 | [Braking In Progress] (BRL) | Braking in progress
| 66 | [Wait for Restart] (TBS) | Wait for motor restart
| 67 | [Cascade Waiting] (STB) | Cascade waiting
| 68 | [Control Supply Loss] (CLA) | Control supply loss
| 69 | [Small Motor Test] (SST) | Small motor test
| 70 | [Demo Mode] (DEMO) | Demo mode
IPM | 0 | [Fixed] (MANU) | Fixed address
| 1 | [BOOTP] (BOOTP) | BOOTP
| 2 | [DHCP] (DHCP) | DHCP
| 3 | [DCP] (DCP) | DCP
LAC | 0 | [Basic] (BAS) | Basic access
| 1 | [Standard] (STD) | Standard access
| 3 | [Expert] (EPR) | Expert access
| 4 | [Services] (SER) | Services
LFT | 0 | [No Error] (NOF) | No error detected
| 1 | [Inhibited Errors] (INH) | Inhibited errors
| 2 | [Control Memory Error] (EEF1) | Control memory error
| 3 | [Incorrect Config] (CFF) | Incorrect configuration
| 4 | [Invalid Configuration] (CFI) | Invalid configuration
| 5 | [Modbus Com Interruption] (SLF1) | Modbus communication interruption
| 6 | [Internal Link Error] (ILF) | Internal communication interruption with option module
| 7 | [Fieldbus Com Interrupt] (CNF) | Fieldbus communication interruption
| 8 | [External Error] (EPF1) | External detected error
| 9 | [Overcurrent] (OCF) | Overcurrent
| 11 | [Phase Inversion] (PIF) | Phase inversion
| 12 | [Lock Rotor Error] (LRF) | Lock rotor error
| 14 | [Mains Direction Error] (PHF2) | Mains direction error
| 15 | [Control Supply Error] (CLF) | Control supply error
| 16 | [Device Overheating] (OHF) | Device overheating
| 17 | [Motor Overload] (OLF) | Motor overload
| 18 | [Mains Freq Error] (FRF) | Mains frequency out of tolerance
| 20 | [Phase Loss] (PHF3) | Phase loss error
| 21 | [Mains Loss] (PHF4) | Mains loss error
| 22 | [Supply Mains UnderV] (USF) | Supply mains undervoltage
| 26 | [Internal Error 1] (INF1) | Internal error 1 (Rating)
| 28 | [Internal Error 3] (INF3) | Internal error 3 (Intern Comm)
| 29 | [Internal Error 4] (INF4) | Internal error 4 (Manufacturing)
| 30 | [Power Memory Error] (EEF2) | Power memory error
| 32 | [Ground Short Circuit] (SCF3) | Ground short circuit
| 34 | [CANopen Com Interrupt] (COF) | CANopen communication interruption
| 35 | [Mains Sync Error] (PHF1) | Mains synchronization error
| 38 | [Fieldbus Error] (EPF2) | External error detected by Fieldbus
| 40 | [Internal Error 8] (INF8) | Internal error 8 (Switching Supply)
| 41 | [In Delta Wiring Error] (DWF) | Inside Delta wiring error
| 42 | [PC Com Interruption] (SLF2) | PC communication interruption
| 45 | [HMI Com Interruption] (SLF3) | HMI communication interruption
| 49 | [CANopen Init Error] (COLF) | CANopen initialization error
| 52 | [Internal Error 10] (INFA) | Internal error 10 (Mains)
| 64 | [Input Contactor] (LCF) | input contactor
| 67 | [Bypass Error] (BYF) | Bypass error
| 68 | [Internal Error 6] (INF6) | Internal error 6 (Option)
| 69 | [Internal Error 14] (INFE) | Internal error 14 (CPU)
| 73 | [Boards Compatibility] (HCF) | Boards compatibility
| 77 | [Conf Transfer Error] (CFI2) | Configuration transfer error
| 99 | [Channel Switch Error] (CSF) | Channel switching detected error
| 100 | [Process Underload] (ULF) | Process underload
| 101 | [Process Overload] (OLC) | Process overload
| 148 | [Too Long Start Error] (TLSF) | Too long start error
| 149 | [Internal Error 21] (INFL) | Internal error 21 (RTC)
| 151 | [Internal Error 15] (INFF) | Internal error 15 (Flash)
| 152 | [Firmware Update Error] (FWER) | Firmware Update error
| 154 | [Internal Error 25] (INFP) | Internal error 25 (Incompatibility CB & SW)
| 187 | [AI1 Th Level Error] (TH1F) | AI1 thermal level error
| 188 | [AI1 Thermal Sensor Error] (T1CF) | Thermal sensor error on AI1
| 201 | [FDR 2 Error] (FDR2) | FDR Eth module error
| 211 | [Security Files Corrupt] (SPFC) | Security files corrupt
| 214 | [Firmware Pairing Error] (FWPF) | Firmware pairing error
| 215 | [Internal Error 35] (INFZ) | Internal error 35 (Invalid firmware version)
| 216 | [Sec Policy Update Err] (SPTF) | Security policy update error
| 217 | [Simu Mains Detected] (SMPF) | Mains detected in simulation mode
| 218 | [No Power Comm Error] (FWMC) | No power communication error
| 219 | [Config Change] (CFF2) | Configuration change
| 224 | [Cust Supply Error] (CPSF) | Customer supply error
L_H | 0 | [Active low] (LO) | Active low
| 1 | [Active high] (HIG) | Active high
NCD | 0 | [Unknown] (UNK) | Unknown rating
| 1 | [17A] (D17) | 17 A
| 2 | [22A] (D22) | 22 A
| 3 | [32A] (D32) | 32 A
| 4 | [38A] (D38) | 38 A
| 5 | [47A] (D47) | 47 A
| 6 | [62A] (D62) | 62 A
| 7 | [75A] (D75) | 75 A
| 8 | [88A] (D88) | 88 A
| 9 | [110A] (C11) | 110 A
| 10 | [140A] (C14) | 140 A
| 11 | [170A] (C17) | 170 A
| 12 | [210A] (C21) | 210 A
| 13 | [250A] (C25) | 250 A
| 14 | [320A] (C32) | 320 A
| 15 | [410A] (C41) | 410 A
| 16 | [480A] (C48) | 480 A
| 17 | [590A] (C59) | 590 A
| 18 | [660A] (C66) | 660 A
| 19 | [790A] (C79) | 790 A
| 20 | [1000A] (M10) | 1000 A
| 21 | [1200A] (M12) | 1200 A
NMTS | 0 | [Boot] (BOOT) | On boot up
| 2 | [Stopped] (STOP) | Stopped
| 1 | [Operation] (OPE) | Operational
| 4 | [Pre-op] (POPE) | Pre operation
NPL | 0 | [High Level] (POS) | High level
| 1 | [Low Level] (NEG) | Low level
N_Y | 0 | [No] (NO) | No
| 1 | [Yes] (YES) | Yes
O_0_4 | 0 | [None] (020)
| 1 | [None] (420)
| 255 | [None] (UNK)
O_AO | 0 | [None] (NO)
| 1 | [None] (OCR)
| 2 | [None] (OTR)
| 3 | [None] (OTH)
| 4 | [None] (OCO)
| 5 | [None] (OPR)
| 255 | [None] (UNK)
O_FCS | 0 | [None] (NO)
| 1 | [None] (YES)
O_FOR | 2 | [None] (8O1)
| 3 | [None] (8E1)
| 4 | [None] (8N1)
| 5 | [None] (8N2)
| 255 | [None] (UNK)
O_FRC | 0 | [None] (AUT)
| 1 | [None] (50)
| 2 | [None] (60)
| 255 | [None] (UNK)
O_LFT | 0 | [None] (NOF)
| 1 | [None] (INH)
| 2 | [None] (INF)
| 3 | [None] (OCF)
| 4 | [None] (PIF)
| 5 | [None] (SLF)
| 6 | [None] (ETF)
| 7 | [None] (STF)
| 8 | [None] (USF)
| 9 | [None] (PHF)
| 10 | [None] (OHF)
| 11 | [None] (LRF)
| 12 | [None] (OLF)
| 13 | [None] (FRF)
| 14 | [None] (ULF)
| 15 | [None] (EEF)
| 16 | [None] (OLC)
| 17 | [None] (CFI)
| 18 | [None] (OTF)
| 20 | [None] (CFF)
| 21 | [None] (CLF)
| 253 | [None] (UNK)
O_LIX | 0 | [None] (NO)
| 1 | [None] (LIA)
| 2 | [None] (LIE)
| 3 | [None] (LIH)
| 4 | [None] (LIL)
| 5 | [None] (LIC)
| 6 | [None] (LII)
| 7 | [None] (LIT)
| 8 | [None] (LIR)
| 9 | [None] (LIS)
| 255 | [None] (UNK)
O_LOX | 0 | [None] (NO)
| 1 | [None] (TAI)
| 2 | [None] (RN1)
| 3 | [None] (AIL)
| 4 | [None] (AUL)
| 5 | [None] (APC)
| 6 | [None] (AS2)
| 7 | [None] (BPS)
| 8 | [None] (R1L)
| 9 | [None] (R1F)
| 255 | [None] (UNK)
O_NCD | 0 | [None] (UNK)
| 1 | [None] (7_5KW)
| 2 | [None] (11KW)
| 3 | [None] (15KW)
| 4 | [None] (18_5KW)
| 5 | [None] (22KW)
| 6 | [None] (30KW)
| 7 | [None] (37KW)
| 8 | [None] (45KW)
| 9 | [None] (55KW)
| 10 | [None] (75KW)
| 11 | [None] (90KW)
| 12 | [None] (110KW)
| 13 | [None] (132KW)
| 14 | [None] (160KW)
| 15 | [None] (220KW)
| 16 | [None] (250KW)
| 17 | [None] (315KW)
| 18 | [None] (355KW)
| 19 | [None] (400KW)
| 20 | [None] (500KW)
| 21 | [None] (630KW)
O_ONOF | 0 | [None] (OFF)
| 1 | [None] (ON)
| 255 | [None] (UNK)
O_PHE | 0 | [None] (NO)
| 1 | [None] (123)
| 2 | [None] (321)
| 255 | [None] (UNK)
O_PHR | 0 | [None] (NO)
| 1 | [None] (123)
| 2 | [None] (321)
| 255 | [None] (UNK)
O_RPR | 0 | [None] (NO)
| 1 | [None] (APH)
| 2 | [None] (TRE)
O_STA | 0 | [None] (NLP)
| 1 | [None] (RDY)
| 2 | [None] (TBS)
| 3 | [None] (HEA)
| 4 | [None] (BRL)
| 5 | [None] (ACC)
| 6 | [None] (DEC)
| 7 | [None] (CLI)
| 8 | [None] (RUN)
| 9 | [None] (NST)
| 10 | [None] (STB)
| 255 | [None] (UNK)
O_STY | 0 | [None] (F)
| 1 | [None] (D)
| 2 | [None] (B)
| 255 | [None] (UNK)
O_TBR | 6 | [None] (4800)
| 7 | [None] (9600)
| 8 | [None] (19200)
| 255 | [None] (UNK)
O_THP | 0 | [None] (OFF)
| 1 | [None] (2)
| 2 | [None] (10A)
| 3 | [None] (10)
| 4 | [None] (15)
| 5 | [None] (20)
| 6 | [None] (25)
| 7 | [None] (30)
| 255 | [None] (UNK)
O_ULL | 0 | [None] (OFF)
| 1 | [None] (DEF)
| 2 | [None] (ALA)
| 255 | [None] (UNK)
O_VCAL | 0 | [None] (UNK)
| 1 | [None] (Q)
| 2 | [None] (Y)
PHE | 0 | [Not Recognized] (NO) | Phase direction not recognized
| 1 | [123] (123) | Phase direction 123
| 2 | [321] (321) | Phase direction 321
PRFL | 0 | [Not Configured] (UNCG) | Not configured
| 1 | [1] (1) | 1
| 100 | [100] (100) | 100
| 101 | [101] (101) | 101
| 102 | [102] (102) | 102
| 106 | [106] (106) | 106
| 107 | [107] (107) | 107
PSA | 0 | [Not Configured] (NO) | Not configured
| 1 | [AI1] (AI1) | AI1 Analog input
| 129 | [Motor Current] (OCR) | Motor current
| 139 | [Motor Power] (OPR) | Motor power
| 140 | [Mot Thermal] (THR) | Motor thermal state
| 159 | [Terminal] (TER) | Terminal
| 163 | [HMI] (LCC) | Local HMI
| 164 | [Ref. Freq-Modbus] (MDB) | Reference frequency via Modbus
| 167 | [Ref. Freq-CANopen] (CAN) | Reference frequency via CANopen
| 169 | [Ref. Freq-Com. Module] (NET) | Reference frequency via Com module
| 401 | [Power Factor] (OCO) | Power factor
| 402 | [Motor Torque] (OTR) | Motor torque
PSL | 0 | [Not Assigned] (NO) | Not assigned
| 1 | [Operating State Fault] (FLT) | Device in operating state "Fault"
| 2 | [Device Running] (RUN) | Device running
| 14 | [Dev Thermal reached] (TAD) | Device thermal threshold reached
| 21 | [Process Undld Warn] (ULA) | Process underload warning
| 22 | [Process Overload Warning] (OLA) | Process overload warning
| 42 | [HMI L/R cmd] (BMP) | HMI local/remote command
| 48 | [Cnfg.0 act.] (CNF0) | Configuration 0 active
| 73 | [Mains Contactor] (LLC) | Mains contactor control
| 80 | [Warning Grp 1] (AG1) | Warning group 1
| 81 | [Warning Grp 2] (AG2) | Warning group 2
| 82 | [Warning Grp 3] (AG3) | Warning group 3
| 87 | [External Error Warning] (EFA) | External error warning
| 88 | [Undervoltage Warning] (USA) | Undervoltage warning
| 91 | [Device Therm Warn] (THA) | Device thermal state warning
| 98 | [Cmd Channel 1] (CD1) | Command channel 1
| 99 | [Cmd Channel 2] (CD2) | Command channel 2
| 127 | [Ready] (RDY) | Ready
| 128 | [Yes] (YES) | Yes
| 129 | [DI1] (LI1) | Digital input 1
| 130 | [DI2] (LI2) | Digital input 2
| 131 | [DI3] (LI3) | Digital input 3
| 132 | [DI4] (LI4) | Digital input 4
| 160 | [CD00] (CD00) | Bit 0 digital input ctrl word
| 161 | [CD01] (CD01) | Bit 1 digital input ctrl word
| 162 | [CD02] (CD02) | Bit 2 digital input ctrl word
| 163 | [CD03] (CD03) | Bit 3 digital input ctrl word
| 164 | [CD04] (CD04) | Bit 4 digital input ctrl word
| 165 | [CD05] (CD05) | Bit 5 digital input ctrl word
| 166 | [CD06] (CD06) | Bit 6 digital input ctrl word
| 167 | [CD07] (CD07) | Bit 7 digital input ctrl word
| 168 | [CD08] (CD08) | Bit 8 digital input ctrl word
| 169 | [CD09] (CD09) | Bit 9 digital input ctrl word
| 170 | [CD10] (CD10) | Bit10 digital input ctrl word
| 171 | [CD11] (CD11) | Bit11 digital input ctrl word
| 172 | [CD12] (CD12) | Bit12 digital input ctrl word
| 173 | [CD13] (CD13) | Bit13 digital input ctrl word
| 174 | [CD14] (CD14) | Bit14 digital input ctrl word
| 175 | [CD15] (CD15) | Bit15 digital input ctrl word
| 176 | [C100] (C100) | Bit 0 Modbus ctrl word
| 177 | [C101] (C101) | Bit 1 Modbus ctrl word
| 178 | [C102] (C102) | Bit 2 Modbus ctrl word
| 179 | [C103] (C103) | Bit 3 Modbus ctrl word
| 180 | [C104] (C104) | Bit 4 Modbus ctrl word
| 181 | [C105] (C105) | Bit 5 Modbus ctrl word
| 182 | [C106] (C106) | Bit 6 Modbus ctrl word
| 183 | [C107] (C107) | Bit 7 Modbus ctrl word
| 184 | [C108] (C108) | Bit 8 Modbus ctrl word
| 185 | [C109] (C109) | Bit 9 Modbus ctrl word
| 186 | [C110] (C110) | Bit 10 Modbus ctrl word
| 187 | [C111] (C111) | Bit 11 Modbus ctrl word
| 188 | [C112] (C112) | Bit 12 Modbus ctrl word
| 189 | [C113] (C113) | Bit 13 Modbus ctrl word
| 190 | [C114] (C114) | Bit 14 Modbus ctrl word
| 191 | [C115] (C115) | Bit 15 Modbus ctrl word
| 192 | [C200] (C200) | Bit 0 CANopen ctrl word
| 193 | [C201] (C201) | Bit 1 CANopen ctrl word
| 194 | [C202] (C202) | Bit 2 CANopen ctrl word
| 195 | [C203] (C203) | Bit 3 CANopen ctrl word
| 196 | [C204] (C204) | Bit 4 CANopen ctrl word
| 197 | [C205] (C205) | Bit 5 CANopen ctrl word
| 198 | [C206] (C206) | Bit 6 CANopen ctrl word
| 199 | [C207] (C207) | Bit 7 CANopen ctrl word
| 200 | [C208] (C208) | Bit 8 CANopen ctrl word
| 201 | [C209] (C209) | Bit 9 CANopen ctrl word
| 202 | [C210] (C210) | Bit 10 CANopen ctrl word
| 203 | [C211] (C211) | Bit 11 CANopen ctrl word
| 204 | [C212] (C212) | Bit 12 CANopen ctrl word
| 205 | [C213] (C213) | Bit 13 CANopen ctrl word
| 206 | [C214] (C214) | Bit 14 CANopen ctrl word
| 207 | [C215] (C215) | Bit 15 CANopen ctrl word
| 208 | [C300] (C300) | Bit 0 Com module ctrl word
| 209 | [C301] (C301) | Bit 1 Com module ctrl word
| 210 | [C302] (C302) | Bit 2 Com module ctrl word
| 211 | [C303] (C303) | Bit 3 Com module ctrl word
| 212 | [C304] (C304) | Bit 4 Com module ctrl word
| 213 | [C305] (C305) | Bit 5 Com module ctrl word
| 214 | [C306] (C306) | Bit 6 Com module ctrl word
| 215 | [C307] (C307) | Bit 7 Com module ctrl word
| 216 | [C308] (C308) | Bit 8 Com module ctrl word
| 217 | [C309] (C309) | Bit 9 Com module ctrl word
| 218 | [C310] (C310) | Bit 10 Com module ctrl word
| 219 | [C311] (C311) | Bit 11 Com module ctrl word
| 220 | [C312] (C312) | Bit 12 Com module ctrl word
| 221 | [C313] (C313) | Bit 13 Com module ctrl word
| 222 | [C314] (C314) | Bit 14 Com module ctrl word
| 223 | [C315] (C315) | Bit 15 Com module ctrl word
| 399 | [Inhibited Errors] (INH) | Inhibited errors
| 402 | [Motor Overload Warn] (OLMA) | Motor overload warning
| 406 | [2nd Mot Param Active] (AS2) | second set of motor parameters activated
| 408 | [End Of Start] (BPS) | End of start
| 409 | [Isolating Relay] (ISOL) | Isolating relay
| 474 | [Temp Sens AI1 Warn] (TS1A) | Temperature sensor AI1 warning
| 485 | [AI1 Th Warning] (TP1A) | AI1 thermal sensor warning
| 492 | [Warning Grp 4] (AG4) | Warning group 4
| 493 | [Warning Grp 5] (AG5) | Warning group 5
| 496 | [Per Type of Stop] (STT) | Per type of stop
PSLIN | 0 | [Not Assigned] (NO) | Not assigned
| 1 | [Operating State Fault] (FLT) | Device in operating state "Fault"
| 98 | [Cmd Channel 1] (CD1) | Command channel 1
| 99 | [Cmd Channel 2] (CD2) | Command channel 2
| 128 | [Yes] (YES) | Yes
| 129 | [DI1] (LI1) | Digital input 1
| 130 | [DI2] (LI2) | Digital input 2
| 131 | [DI3] (LI3) | Digital input 3
| 132 | [DI4] (LI4) | Digital input 4
| 160 | [CD00] (CD00) | Bit 0 digital input ctrl word
| 161 | [CD01] (CD01) | Bit 1 digital input ctrl word
| 162 | [CD02] (CD02) | Bit 2 digital input ctrl word
| 163 | [CD03] (CD03) | Bit 3 digital input ctrl word
| 164 | [CD04] (CD04) | Bit 4 digital input ctrl word
| 165 | [CD05] (CD05) | Bit 5 digital input ctrl word
| 166 | [CD06] (CD06) | Bit 6 digital input ctrl word
| 167 | [CD07] (CD07) | Bit 7 digital input ctrl word
| 168 | [CD08] (CD08) | Bit 8 digital input ctrl word
| 169 | [CD09] (CD09) | Bit 9 digital input ctrl word
| 170 | [CD10] (CD10) | Bit10 digital input ctrl word
| 171 | [CD11] (CD11) | Bit11 digital input ctrl word
| 172 | [CD12] (CD12) | Bit12 digital input ctrl word
| 173 | [CD13] (CD13) | Bit13 digital input ctrl word
| 174 | [CD14] (CD14) | Bit14 digital input ctrl word
| 175 | [CD15] (CD15) | Bit15 digital input ctrl word
| 177 | [C101] (C101) | Bit 1 Modbus ctrl word
| 178 | [C102] (C102) | Bit 2 Modbus ctrl word
| 179 | [C103] (C103) | Bit 3 Modbus ctrl word
| 180 | [C104] (C104) | Bit 4 Modbus ctrl word
| 181 | [C105] (C105) | Bit 5 Modbus ctrl word
| 182 | [C106] (C106) | Bit 6 Modbus ctrl word
| 183 | [C107] (C107) | Bit 7 Modbus ctrl word
| 184 | [C108] (C108) | Bit 8 Modbus ctrl word
| 185 | [C109] (C109) | Bit 9 Modbus ctrl word
| 186 | [C110] (C110) | Bit 10 Modbus ctrl word
| 187 | [C111] (C111) | Bit 11 Modbus ctrl word
| 188 | [C112] (C112) | Bit 12 Modbus ctrl word
| 189 | [C113] (C113) | Bit 13 Modbus ctrl word
| 190 | [C114] (C114) | Bit 14 Modbus ctrl word
| 191 | [C115] (C115) | Bit 15 Modbus ctrl word
| 193 | [C201] (C201) | Bit 1 CANopen ctrl word
| 194 | [C202] (C202) | Bit 2 CANopen ctrl word
| 195 | [C203] (C203) | Bit 3 CANopen ctrl word
| 196 | [C204] (C204) | Bit 4 CANopen ctrl word
| 197 | [C205] (C205) | Bit 5 CANopen ctrl word
| 198 | [C206] (C206) | Bit 6 CANopen ctrl word
| 199 | [C207] (C207) | Bit 7 CANopen ctrl word
| 200 | [C208] (C208) | Bit 8 CANopen ctrl word
| 201 | [C209] (C209) | Bit 9 CANopen ctrl word
| 202 | [C210] (C210) | Bit 10 CANopen ctrl word
| 203 | [C211] (C211) | Bit 11 CANopen ctrl word
| 204 | [C212] (C212) | Bit 12 CANopen ctrl word
| 205 | [C213] (C213) | Bit 13 CANopen ctrl word
| 206 | [C214] (C214) | Bit 14 CANopen ctrl word
| 207 | [C215] (C215) | Bit 15 CANopen ctrl word
| 209 | [C301] (C301) | Bit 1 Com module ctrl word
| 210 | [C302] (C302) | Bit 2 Com module ctrl word
| 211 | [C303] (C303) | Bit 3 Com module ctrl word
| 212 | [C304] (C304) | Bit 4 Com module ctrl word
| 213 | [C305] (C305) | Bit 5 Com module ctrl word
| 214 | [C306] (C306) | Bit 6 Com module ctrl word
| 215 | [C307] (C307) | Bit 7 Com module ctrl word
| 216 | [C308] (C308) | Bit 8 Com module ctrl word
| 217 | [C309] (C309) | Bit 9 Com module ctrl word
| 218 | [C310] (C310) | Bit 10 Com module ctrl word
| 219 | [C311] (C311) | Bit 11 Com module ctrl word
| 220 | [C312] (C312) | Bit 12 Com module ctrl word
| 221 | [C313] (C313) | Bit 13 Com module ctrl word
| 222 | [C314] (C314) | Bit 14 Com module ctrl word
| 223 | [C315] (C315) | Bit 15 Com module ctrl word
PST | 0 | [Stop Key No Priority] (NO) | Stop key no priority
| 1 | [Stop Key Priority] (YES) | Stop key priority
RDS | 0 | [Auto] (AUTO) | Auto detected
| 1 | [10M. full] (10F) | 10Mbps full duplex
| 2 | [10M. half] (10H) | 10Mbps half duplex
| 3 | [100M. full] (100F) | 100Mbps full duplex
| 4 | [100M. half] (100H) | 100Mbps half duplex
RPR | 0 | [No] (NO) | No
| 1 | [Reset Consumption] (APH) | Reset consumption counters
| 2 | [Reset Run Time] (RTH) | Reset run time
| 3 | [Reset Tot Run Time] (RTHI) | Reset total run time
| 4 | [Reset Power On Time] (PTH) | Reset power ON time
| 8 | [Reset Tot Pw On Time] (PTHI) | Reset total power ON time
| 11 | [Reset Start Count] (NSM) | Reset start counter
| 12 | [Reset Start Total] (NSMI) | Reset total start counter
| 51 | [Reset Bypass Count] (BPCN) | Reset bypass counter
| 52 | [Reset Bypass Total] (BPTN) | Reset total bypass counter
| 64 | [Reset All (Service)] (ALL) | Reset all counters including service
| 65 | [Reset All] (ALLC) | Reset all counters
SCAL | 0 | [Unknown] (UNK) | Unknown range
| 2 | [208..690V] (Y) | 208..690V
SCS | 0 | [No] (NO) | No
| 1 | [Config 0] (STR0) | Save configuration 0
| 2 | [Config 1] (STR1) | Save configuration 1
| 3 | [Config 2] (STR2) | Save configuration 2
| 4 | [Config 3] (STR3) | Config 3
SFDR | 0 | [Initialization] (INIT) | Initialization
| 1 | [Not Active] (IDLE) | Not active
| 2 | [Operational] (OPE) | Operational
| 4 | [Ready] (RDY) | Ready
| 5 | [IP Configuration] (IPC) | IP configuration
| 7 | [Not Configured] (UNCF) | Not configured
| 8 | [Reading Configuration] (GET) | Reading configuration
| 9 | [Writing Configuration] (SET) | Writing configuration
| 10 | [Applying Configuration] (APP) | Applying configuration
STT | 0 | [Freewheel] (F) | Freewheel
| 1 | [Deceleration] (D) | Controlled deceleration
| 2 | [Braking] (B) | Dynamic braking
S_PHR | 0 | [No] (NO) | No monitoring
| 1 | [123] (123) | 123 phase direction
| 2 | [321] (321) | 321 phase direction
TBR | 4 | [Automatic] (AUTO) | Automatic
| 8 | [300 bps] (300) | 300 bps
| 12 | [600 bps] (600) | 600 bps
| 16 | [1.2 Kbps] (1200) | 1.2 Kbps
| 20 | [2.4 Kbps] (2400) | 2.4 Kbps
| 24 | [4800 bps] (4800) | 4800 bps
| 28 | [9600 bps] (9600) | 9600 bps
| 30 | [10 Kbps] (10000) | 10 Kbps
| 32 | [19200 bps] (19200) | 19200 bps
| 34 | [20 Kbps] (20000) | 20 Kbps
| 35 | [28.8 Kbps] (28800) | 28.8 Kbps
| 36 | [38.4 Kbps] (38400) | 38.4 Kbps
| 37 | [45.45 Kbps] (45450) | 45.45 Kbps
| 38 | [50 Kbps] (50000) | 50 Kbps
| 40 | [57.6 Kbps] (57600) | 57.6 Kbps
| 41 | [76.8 Kbps] (76800) | 76.8 Kbps
| 42 | [93.75 Kbps] (93750) | 93.75 Kbps
| 44 | [100 Kbps] (100K) | 100 Kbps
| 48 | [115.2 Kbps] (115K2) | 115.2 Kbps
| 52 | [125 Kbps] (125K) | 125 Kbps
| 53 | [156 Kbps] (156K) | 156 Kbps
| 54 | [187.5 Kbps] (187K5) | 187.5 Kbps
| 56 | [230.4 Kbps] (230K4) | 230.4 Kbps
| 60 | [250 Kbps] (250K) | 250 Kbps
| 61 | [256 Kbps] (256K) | 256 Kbps
| 64 | [460.8 Kbps] (460K8) | 460.8 Kbps
| 68 | [500 Kbps] (500K) | 500 Kbps
| 69 | [625 Kbps] (625K) | 625 Kbps
| 70 | [800 Kbps] (800K) | 800 Kbps
| 72 | [921.6 Kbps] (921K6) | 921.6 Kbps
| 76 | [1 Mbps] (1M) | 1 Mbps
| 80 | [1.5 Mbps] (1M5) | 1.5 Mbps
| 81 | [2.5 Mbps] (2M5) | 2.5 Mbps
| 82 | [3 Mbps] (3M) | 3 Mbps
| 83 | [6 Mbps] (6M) | 6 Mbps
| 84 | [10 Mbps] (10M) | 10 Mbps
| 86 | [5 Mbps] (5M) | 5 Mbps
| 88 | [12 Mbps] (12M) | 12 Mbps
| 92 | [100 Mbps] (100M) | 100 Mbps
THP | 0 | [No Protection] (NO) | No protection
| 1 | [Class 2] (2) | Class 2
| 2 | [Class 10A] (10A) | Class 10A
| 3 | [Class 10E] (10E) | Class 10E
| 4 | [Class 15] (15) | Class 15
| 5 | [Class 20E] (20E) | Class 20E
| 6 | [Class 25] (25) | Class 25
| 7 | [Class 30E] (30E) | Class 30E
TIMF | 0 | [24h] (24) | 24h
| 1 | [12h] (12) | 12h
TWO | 0 | [OFF] (LOW) | ModBus Word Order OFF
| 1 | [ON] (HIGH) | Modbus Word Order ON

## Registers
CMI |  | Bit 0 | Factory setting command (active at 1).
|  | Bit 1 | Save configuration to non-volatile memory command (active at 1).
This Bit automatically changes to 0 after the request is taken into account. The command is only active if the device is stopped, and not in "5-Operation enabled" state.
Note: If CMI is a periodic network variable, the PLC program must write it to 0 after the first request is taken into account. The life of the non volatile memory is limited to 100,000 write operations.
|  | Bit 2 | Restore saved configuration (active at 1).
This Bit doesn't return to 0 after treatment.
|  | Bit 3 | External error (active at 1).
|  | Bit 4 | Reserved (= 0).
|  | Bit 5 | Reserved (= 0).
|  | Bit 6 | Reserved (= 0).
|  | Bit 7 | Reserved (= 0).
|  | Bit 8 | Reserved (= 0).
|  | Bit 9 | Reserved (= 0).
|  | Bit 10 | Reserved (= 0).
|  | Bit 11 | Reserved (= 0).
|  | Bit 12 | Reserved (= 0).
|  | Bit 13 | Reserved (= 0).
|  | Bit 14 | Reserved (= 0).
|  | Bit 15 | Parameter consistency check
= 0: The check is activated. Each time a parameter is written, the device checks the relationship between the written parameter and the configuration in the device..
= 1: The check is deactivated. The device is locked in stop mode. In this device state, the configuration can be written parameter by parameter and the device does not modify the values that are written.
The switch from 1 to 0 triggers a calculation of the consistency of the configuration. Some parameters can be modified automatically by the device.
CMD | Possible values in SE8 profile:
CMP0 |  | Bit 0 | Switch on/Contactor command.
CMP1 |  | Bit 1 | Disable voltage (Active at 1)/Authorization to supply AC power.(Active at 0)
CMP2 |  | Bit 2 | Quick stop.
CMP3 |  | Bit 3 | Enable operation/Run command.
CMP4 |  | Bit 4 | Reserved (set to 0).
CMP5 |  | Bit 5 | Reserved (set to 0).
CMP6 |  | Bit 6 | Reserved (set to 0).
CMP7 |  | Bit 7 | Fault reset/error cleared on transition 0 to 1 .
CMP8 |  | Bit 8 | Command released (0: "In LINE mode" / 1: "In LOCAL mode").
CMP9 |  | Bit 9 | Reserved (set to 0).
CMPA |  | Bit 10 | Reserved (set to 0).
CMPB |  | Bit 11 | Reserved (set to 0).
CMPC |  | Bit 12 | Halt Stop according to the [Type of stop] (Stt) parameter without leaving the Operation enabled state.
CMPD |  | Bit 13 | Halt Stop according to the braking stop without leaving the Operation enabled state.
CMPE |  | Bit 14 | Halt Stop according to the deceleration stop without leaving the Operation enabled state.
CMPF |  | Bit 15 | LOCAL/LINE mode selection (0: "In LINE mode" / 1: "In LOCAL mode").
CMD1 | Possible values in Standard profile:
CMD2 |  | Bit 0 | Switch on/Contactor command.
CMD3 |  | Bit 1 | Disable voltage/Authorization to supply AC power.
|  | Bit 2 | Quick stop.
|  | Bit 3 | Enable operation/Run command.
|  | Bit 4 | Reserved (set to 0).
|  | Bit 5 | Reserved (set to 0).
|  | Bit 6 | Reserved (set to 0).
|  | Bit 7 | Fault reset/error cleared on transition 0 to 1 .
|  | Bit 8 | Halt Stop according to the [Type of stop] (Stt) parameter without leaving the Operation enabled state.
|  | Bit 9 | Reserved (set to 0).
|  | Bit 10 | Reserved (set to 0).
|  | Bit 11 | Can be assigned to commands.
|  | Bit 12 | Can be assigned to commands.
|  | Bit 13 | Braked stop request / User bit (active when set to 1).
|  | Bit 14 | Decelerated stop request /User bit (active when set to 1).
|  | Bit 15 | Can be assigned to commands.
ETA | Possible values in CiA402 profile:
EP0 |  | Bit 0 | = 1: "Ready to switch on", awaiting power section line supply
EP1 |  | Bit 1 | = 1: "Switched on", ready
EP2 |  | Bit 2 | = 1: "Operation enabled", running
EP3 |  | Bit 3 | = 1: Fault detection
EP4 |  | Bit 4 | "Voltage enabled", power part connected to supply mains
EP5 |  |  | = 0: Power part not connected to supply mains
EP6 |  |  | = 1: Power part connected to supply mains
EP7 |  |  | When the device is powered by the power section only, this bit is always at 1.
EP8 |  | Bit 5 | Bit 5: = 0: Quick stop
EP9 |  | Bit 6 | Bit 6: = 1: "Switched on disabled", power section line supply locked
EPA |  | Bit 7 | Bit 7: Warning
EPB |  |  | = 0: No warning
EPC |  |  | = 1: Warning active
EPD |  | Bit 8 | Bit 8: Reserved (= 0)
EPE |  | Bit 9 | Bit 9: Remote: command via fieldbus
EPF |  |  | = 0: Command given via the graphic display terminal or remote display terminal
ETAD |  |  | = 1: Command via fieldbus
|  | Bit 10 | Bit 10: Reserved (= 0)
|  | Bit 11 | Bit 11: Reserved (= 0)
|  | Bit 12 | Bit 12: Reserved (= 0)
|  | Bit 13 | Bit 13: Reserved (= 0)
|  | Bit 14 | Bit 14: "Stop key", STOP via stop key
= 0: STOP key not active
= 1: Stop triggered by the STOP key on the graphic display terminal or the remote display terminal
|  | Bit 15 | Bit 15: "Direction", direction of rotation
= 0: Forward rotation at output
= 1: Reverse rotation at output
The combination of Bits 0, 1, 2, 4, 5 and 6 defines the state in the DSP 402 state chart (refer to fieldbus manuals).
ETI |  | Bit 0 | = 1: Access to the non-volatile memory in progress
IP0 |  | Bit 1 | = 0: No parameter consistency check
IP1 |  |  | = 1: Parameter consistency check
IP2 |  | Bit 2 | = 0: The device is not in operating state "Fault" or in operating state "Fault" and the error is active
IP3 |  |  | = 1: The device is in operating state "Fault" and the error is no longer active (not reset))
IP4 |  | Bit 3 | = 1: Preheating is active.
IP5 |  | Bit 4 | = 1: The device is in running mode
IP6 |  | Bit 5 | = 1: Braking active
IP7 |  | Bit 6 | = 0: device in transient state
IP8 |  |  | = 1: device in steady state
IP9 |  | Bit 7 | = 1: Motor thermal state threshold reached for the active motor
IPA |  | Bit 8 | Bit 8: Reserved (= 0).
IPB |  | Bit 9 | = 1: Acceleration active
IPC |  | Bit 10 | = 1: Deceleration active
IPD |  | Bit 11 | = 1: Current limit active
IPE |  | Bit 12 | = 1: Torque limit active
IPF |  | Bit 13 to 14 | bit 13 = 0 and bit 14 = 0: Device controled by terminal
bit 13 = 1 and bit 14 = 0: Device controled by remote keypad
bit 13 = 0 and bit 14 = 1: Device controled by Modbus
bit 13 = 1 and bit 14 = 1: Device controled by CANopen or the network card
|  | Bit 15 | = 0: Forward operation applied before the ramp
= 1: Reverse operation applied before the ramp
CCC |  | Bit 0 | = 1 : Terminal board
|  | Bit 2 | = 1 : Deported keypad
|  | Bit 3 | = 1 : Modbus
|  | Bit 6 | = 1 : CANopen
|  | Bit 9 | = 1 : COM option board
|  | Bit 14 | = 1 : Indus
|  | Bit 15 | = 1 : SoMove
IL1R |  | Bit 0 | "LI1" Digital inputs real image
|  | Bit 1 | "LI2" Digital inputs real image
|  | Bit 2 | "LI3" Digital inputs real image
|  | Bit 3 | "LI4" Digital inputs real image
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
OL1R |  | Bit 0 | "R1" relay real image
|  | Bit 1 | "R2" relay real image
|  | Bit 2 | "R3" relay real image
|  | Bit 8 | "DO1" logic outputs real image
|  | Bit 9 | "DO2" logic outputs real image
CIC |  | Bit 0 | = 1: Change of rating.
|  | Bit 1 | = 1: The fielbus module has been added.
|  | Bit 2 | = 1: The fielbus module has been removed.
|  | Bit 3 | = 1: Loaded config invalid.
|  | Bit 4 | = 1: The fielbus module has been changed.
|  | Bit 5 | Reserved (=0).
|  | Bit 6 | Reserved (=0).
|  | Bit 7 | Reserved (=0).
|  | Bit 8 | = 1: The IO module has been added.
|  | Bit 9 | = 1: The IO module has been removed.
|  | Bit 10 | = 1: The IO module has been changed.
|  | Bit 11 | = 1: The encoder module has been added.
|  | Bit 12 | = 1: The encoder module has been removed.
|  | Bit 13 | = 1: The encoder module has been changed.
|  | Bit 14 | = 1: The control board has been changed.
If one of these events occurs, the device will trigger an error [Invalid configiguration] (CFI) and then automatically restore the factory settings.
AGP0 |  |  | Same as AGS
AGP1 |  |  | Same as AGS
AGP2 |  |  | Same as AGS
AGP3 |  |  | Same as AGS
AGP4 |  |  | Same as AGS
AGP5 |  |  | Same as AGS
AGP6 |  |  | Same as AGS
AGP7 |  |  | Same as AGS
AGP8 |  |  | Same as AGS
FRY |  | Bit 0 | = 1 : All parameters
|  | Bit 1 | = 1 : Device configuration
|  | Bit 2 | Reserved
|  | Bit 3 | = 1 : Motor parameters
|  | Bit 4 | = 1 : Communication menu
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | = 1 : Display menu
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | = 1 : Communication option parameters
IL1I |  | Bit 0 | "LI1" Digital inputs physical image
|  | Bit 1 | "LI2" Digital inputs physical image
|  | Bit 2 | "LI3" Digital inputs physical image
|  | Bit 3 | "LI4" Digital inputs physical image
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
PEV1 |  | Bit 0 | = 1 : first mapped Object
|  | Bit 1 | = 1 : second mapped Object
|  | Bit 2 | = 1 : third mapped Object
|  | Bit 3 | = 1 : fourth mapped Object
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
PEV2 |  | Bit 0 | = 1 : first mapped Object
|  | Bit 1 | = 1 : second mapped Object
|  | Bit 2 | = 1 : third mapped Object
|  | Bit 3 | = 1 : fourth mapped Object
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
PEV3 |  | Bit 0 | = 1 : first mapped Object
|  | Bit 1 | = 1 : second mapped Object
|  | Bit 2 | = 1 : third mapped Object
|  | Bit 3 | = 1 : fourth mapped Object
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
PEV4 |  | Bit 0 | = 1 : first mapped Object
|  | Bit 1 | = 1 : second mapped Object
|  | Bit 2 | = 1 : third mapped Object
|  | Bit 3 | = 1 : fourth mapped Object
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
ST02 |  | Bit 0 | (CNF0) : Configuration 1 is used
ST03 |  | Bit 0 | (FLO) : Device in forced local mode
|  | Bit 4 | (CD1) : Command channel is channel 1
|  | Bit 5 | (CD2) : Command channel is channel 2
|  | Bit 8 | (CCS) : Command channel : 0-> channel 1, 1-> channel 2
|  | Bit 9 | (BMP) : Bump Less Channel
ST04 |  | Bit 0 | (FLT) : Device is in error state
|  | Bit 1 | (AUTO) : Automatic restart attempts in progress
|  | Bit 2 | (RDY) : Device is in ready state
|  | Bit 3 | (RUN) : A gating order is set (there is potentially current in the motor)
|  | Bit 10 | (STT) : Reaction on event / Stop on STT without tripping in fault
|  | Bit 13 | (BYP) : Starter in Bypass
|  | Bit 14 | (BRL) : Starter Braking Active
|  | Bit 15 | (SDY) : Starter in Steady State
ST05 |  | Bit 0 | (LLC) : The device asks to close the line contactor
|  | Bit 13 | (BPS) : Bypass relay activated
|  | Bit 14 | (BPA) : Bypass alarm
ST06 |  | Bit 0 | (ACC) : Motor in acceleration
|  | Bit 1 | (DEC) : Motor in deceleration
|  | Bit 14 | (OLMA) : Motor overload
|  | Bit 15 | (TBS) : Tme before restarting
ST07 |  | Bit 0 | (AG1) : One of the alarm of alarm group 1 is active
|  | Bit 1 | (AG2) : One of the alarm of alarm group 2 is active
|  | Bit 2 | (AG3) : One of the alarm of alarm group 3 is active
|  | Bit 3 | (AG4) : One of the alarm of alarm group 4 is active
|  | Bit 4 | (AG5) : One of the alarm of alarm group 5 is active
ST11 |  | Bit 4 | (TP1A) : Temperature Protection on input 1 Alarm
|  | Bit 8 | (TS1A) : Temperature Sensor on input 1 Alarm
ST13 |  | Bit 0 | (THA) : Device overheating alarm is raised
|  | Bit 5 | (EFA) : External alarm is raised
|  | Bit 6 | (USA) : Undervoltage alarm is raised
|  | Bit 12 | (INH) : Inhibition alarm
|  | Bit 13 | (RBLA) : Battery level alarm
|  | Bit 14 | (RBNA) : Battery not present alarm
|  | Bit 15 | (RTCA) : RTC alarm
ST15 |  | Bit 4 | (ULA) : Underload is detected
|  | Bit 5 | (OLA) : Overload is detected
|  | Bit 6 | (CLI) : Current or torque limitation is running
ST16 |  | Bit 1 | (TAD) : Device Thermal Threshold Reached function result
ST17 |  | Bit 5 | (SLLA) : Modbus communication interruption error when ignored
|  | Bit 6 | (CLLA) : Fieldbus communication error when ignored
|  | Bit 7 | (COLA) : CANOpen communication loss error when ignored
CIC2 |  |  | On power-up, read CIC :
If CIC and CIC2 = 0 -> Ok
If CIC or CIC2 not 0 -> malfunction
Write FCS = "INI" to return to factory setting
|  | Bit 0 | = 1 : SFTY option card added
|  | Bit 1 | = 1 : SFTY option card removed
|  | Bit 2 | = 1 : SFTY option card changed
|  | Bit 3 | Reserved
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
AGP9 |  |  | Same as AGS
AGPA |  |  | Same as AGS
AGPB |  |  | Same as AGS
AGPC |  |  | Same as AGS
AGPD |  |  | Same as AGS
AGPE |  |  | Same as AGS
AGPF |  |  | Same as AGS
O_CMD |  | Bit 0 | Switch on/Contactor command.
|  | Bit 1 | Disable voltage (Active at 1)/Authorization to supply AC power.(Active at 0)
|  | Bit 2 | Quick stop.
|  | Bit 3 | Enable operation/Run command.
|  | Bit 4 | Reserved (set to 0).
|  | Bit 5 | Reserved (set to 0).
|  | Bit 6 | Reserved (set to 0).
|  | Bit 7 | Fault reset/error cleared on transition 0 to 1 .
|  | Bit 8 | Command released (0: "In LINE mode" / 1: "In LOCAL mode").
|  | Bit 9 | Reserved (set to 0).
|  | Bit 10 | Reserved (set to 0).
|  | Bit 11 | Reserved (set to 0).
|  | Bit 12 | Halt Stop according to the [Type of stop] (Stt) parameter without leaving the Operation enabled state.
|  | Bit 13 | Halt Stop according to the braking stop without leaving the Operation enabled state.
|  | Bit 14 | Halt Stop according to the deceleration stop without leaving the Operation enabled state.
|  | Bit 15 | LOCAL/LINE mode selection (0: "In LINE mode" / 1: "In LOCAL mode").
O_CMI |  | Bit 0 | Factory setting command on transition 0 to 1.
|  | Bit 1 | Save configuration to non-volatile memory command on transition 0 to 1.
|  | Bit 2 | Restore saved configuration command on transition 0 to 1.
|  | Bit 3 | = 1: External error..
|  | Bit 4 | Reserved (set to 0).
|  | Bit 5 | = 1: Switch to second set of motor parameters.
|  | Bit 6 | Reserved (set to 0).
|  | Bit 7 | Reserved (set to 0).
|  | Bit 8 | Reserved (set to 0).
|  | Bit 9 | Reserved (set to 0).
|  | Bit 10 | = 1: Motor preheating request.
|  | Bit 11 | = 1: Disable protection request.
|  | Bit 12 | Reserved (set to 0).
|  | Bit 13 | = 1: Lock starter on stopping request.
|  | Bit 14 | = 1: Disable line monitoring.
|  | Bit 15 | = 1: Disable parameter consistency check.
O_ETA |  | Bit 0 | = 1: "Ready to switch on", awaiting power section line supply
|  | Bit 1 | = 1: "Switched on", ready
|  | Bit 2 | = 1: "Operation enabled", running
|  | Bit 3 | = 1: Fault detection
|  | Bit 4 | = 1: Power part connected to supply mains
|  | Bit 5 | = 0: Quick stop
|  | Bit 6 | = 1: "Switched on disabled", power section line supply locked
|  | Bit 7 | = 1: Alarm present
|  | Bit 8 | Reserved (set to 0).
|  | Bit 9 | = 0: Forced local active
|  | Bit 10 | Reserved (set to 0).
|  | Bit 11 | Reserved (set to 0).
|  | Bit 12 | Reserved (set to 0).
|  | Bit 13 | Reserved (set to 0).
|  | Bit 14 | Reserved (set to 0).
|  | Bit 15 | Reserved (set to 0).
O_ETA2 |  | Bit 0 | = 1: "Ready to switch on"
|  | Bit 1 | = 1: "Switched on"
|  | Bit 2 | = 1: "Operation enabled"
|  | Bit 3 | = 1: "Malfunction"
|  | Bit 4 | = 1: No power/ Voltage disabled
|  | Bit 5 | = 0: "Quick stop" active
|  | Bit 6 | = 1: "Switch on disabled"
|  | Bit 7 | = 1: Alarm present
|  | Bit 8 | Reserved for Drivecom
|  | Bit 9 | = 0: FORCED LOCAL active
|  | Bit 10 | Reserved (set to 0)
|  | Bit 11 | Reserved (set to 0)
|  | Bit 12 | Reserved (set to 0)
|  | Bit 13 | Reserved (set to 0)
|  | Bit 14 | Reserved (set to 0)
|  | Bit 15 | Reserved (set to 0)
O_ETI |  | Bit 0 | Write parameter authorization
= 0: Authorized
= 1: Not authorized
|  | Bit 1 | = 1: Parameter consistency check
|  | Bit 2 | = 1: Starter reset authorization
|  | Bit 3 | = 1: Preheating is active.
|  | Bit 4 | = 1: The device is in running mode
|  | Bit 5 | = 1: Braking active
|  | Bit 6 | = 0: Device in transient state
= 1: Device in steady state
|  | Bit 7 | = 1: Motor thermal state threshold reached for the active motor
|  | Bit 8 | Reserved (set to 0).
|  | Bit 9 | = 1: Acceleration active
|  | Bit 10 | = 1: Deceleration active
|  | Bit 11 | = 1: Current limit active
|  | Bit 12 | = 1: Torque limit active
|  | Bit 13 to 14 | bit 13 = 0 and bit 14 = 0: LOCAL mode or FORCED LOCAL mode
bit 13 = 1 and bit 14 = 0: Not possible state
bit 13 = 0 and bit 14 = 1: LINE mode (ATS46 profile)
bit 13 = 1 and bit 14 = 1: LINE mode (Drivecom profile)
|  | Bit 15 | Reserved (set to 0).
O_ETI8 |  | Bit 0 | Write parameter authorization
= 0: Authorized
= 1: Not authorized
|  | Bit 1 | = 1: Parameter consistency check
|  | Bit 2 | = 1: Starter reset authorization
|  | Bit 3 | = 1: Preheating is active.
|  | Bit 4 | = 1: The device is in running mode
|  | Bit 5 | = 1: Braking active
|  | Bit 6 | = 0: Device in transient state
= 1: Device in steady state
|  | Bit 7 | = 1: Motor thermal state threshold reached for the active motor
|  | Bit 8 | Reserved (set to 0).
|  | Bit 9 | = 1: Acceleration active
|  | Bit 10 | = 1: Deceleration active
|  | Bit 11 | = 1: Current limit active
|  | Bit 12 | = 1: Torque limit active
|  | Bit 13 to 14 | bit 13 = 0 and bit 14 = 0: LOCAL mode or FORCED LOCAL mode
bit 13 = 1 and bit 14 = 0: Not possible state
bit 13 = 0 and bit 14 = 1: LINE mode (ATS46 profile)
bit 13 = 1 and bit 14 = 1: LINE mode (Drivecom profile)
|  | Bit 15 | Reserved (set to 0).
O_ETI2 |  | Bit 0 | Reserved (set to 0).
|  | Bit 1 | Reserved (set to 0).
|  | Bit 2 | Reserved (set to 0).
|  | Bit 3 | Reserved (set to 0).
|  | Bit 4 | Reserved (set to 0).
|  | Bit 5 | Reserved (set to 0).
|  | Bit 6 | = 1: Current overload threshold (CTD) reached
|  | Bit 7 | Reserved (set to 0).
|  | Bit 8 | Reserved (set to 0).
|  | Bit 9 | Reserved (set to 0).
|  | Bit 10 | = 1: Underload threshold
|  | Bit 11 | = 1: PTC probe motor thermal protection threshold reached
|  | Bit 12 | = 1: Use of second motor configuration
|  | Bit 13 | = 0: Time delay before starting complete
= 1: active
|  | Bit 14 | = 1: Cascade operation
|  | Bit 15 | Reserved (set to 0).
O_ET28 |  | Bit 0 | Reserved (set to 0).
|  | Bit 1 | Reserved (set to 0).
|  | Bit 2 | Reserved (set to 0).
|  | Bit 3 | Reserved (set to 0).
|  | Bit 4 | Reserved (set to 0).
|  | Bit 5 | Reserved (set to 0).
|  | Bit 6 | = 1: Current overload threshold (CTD) reached
|  | Bit 7 | Reserved (set to 0).
|  | Bit 8 | Reserved (set to 0).
|  | Bit 9 | Reserved (set to 0).
|  | Bit 10 | = 1: Underload threshold
|  | Bit 11 | = 1: PTC probe motor thermal protection threshold reached
|  | Bit 12 | = 1: Use of second motor configuration
|  | Bit 13 | = 0: Time delay before starting complete
= 1: active
|  | Bit 14 | = 1: Cascade operation
|  | Bit 15 | Reserved (set to 0).
O_IOL |  | Bit 0 | Logic input LI3 (0 - low state / 1 - high state)
|  | Bit 1 | Logic output LO1 (0 - low state / 1 - high state)
|  | Bit 2 | Logic output LO2 (0 - low state / 1 - high state)
|  | Bit 3 | Relay R1 (0 - open / 1 - closed)
|  | Bit 4 | Relay R2 (0 - open / 1 - closed)
|  | Bit 5 | Reserved (set to 0).
|  | Bit 6 | Logic input LI2 (0 - low state / 1 - high state)
|  | Bit 7 | Logic input LI1 (0 - low state / 1 - high state)
|  | Bit 8 | Reserved (set to 0).
|  | Bit 9 | Logic input LI4 (0 - low state / 1 - high state)
|  | Bit 10 | Relay R3 (0 - open / 1 - closed)
|  | Bit 11 | Reserved (set to 0).
|  | Bit 12 | Reserved (set to 0).
|  | Bit 13 | Reserved (set to 0).
|  | Bit 14 | Reserved (set to 0).
|  | Bit 15 | Reserved (set to 0).
O_EP1 |  | Bit 0 | = 1: Power part connected to supply mains
O_EP2 |  | Bit 1 | = 1: Torque limit active
O_EP3 |  | Bit 2 | = 1: "Switched on disabled", power section line supply locked
O_EP4 |  | Bit 3 | = 0: Forced local active
O_EP5 |  | Bit 4 | = 1: Preheating is active.
|  | Bit 5 | = 1: The device is in running mode
|  | Bit 6 | = 1: Braking active
|  | Bit 7 | = 1: Motor thermal state threshold reached for the active motor
|  | Bit 8 | = 1: Acceleration active
|  | Bit 9 | = 1: Deceleration active
|  | Bit 10 | = 1: Current limit active
|  | Bit 11 | = 0 : Time delay before starting complete
=1 : active
|  | Bit 12 to 13 | bit 12 = 0 and bit 13 = 0: LOCAL mode or FORCED LOCAL mode
bit 12 = 1 and bit 13 = 0: Not possible state
bit 12 = 0 and bit 13 = 1: LINE mode (ATS46 profile)
bit 12 = 1 and bit 13 = 1: LINE mode (Drivecom profile)
|  | Bit 14 | = 1: Use of second motor configuration
|  | Bit 15 | = 1: Cascade operation